|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Humidifier Survey Checklist Page …… of…….** | | | | | | | | | | | | | | | |
| **Engineer** | | | | **Type of visit:** | | | | | **Date:** | | | | | **Building ref** | |
| **Item No.** | **Equipment** | **Serial number** | **Ref/ location** | **Hours** | **Service counter (next service hrs)** | **Last service date** | **Units status On/ Off** | **Fault history** | **Installation checked** | **Inspection for leaks**  **(unit off)** | **Drain valve/ pump check** | **Basic operation check** | **Parts required Y/ N** | **Works required (PM No parts/ PM parts/ repair)** | **Comments (inc parts & work)**  **(add if photo taken)** |
| 1 | EL 5kg | 1181350 | Plant Rm 3 | 136.9 | 2363 | n/a | On | n/a | Y | Y | Y | Y | N | PM | Relatively new unit, low run hours. |
| 2 | ELMC 5kg | 90869 | Plant Rm 3 | ? | ? | n/a | Off | n/a | Y | Y | N | N | Y | PM Repair | Unit off partially dismantled. Parts – Drain Vv. Older unit. |
| 3 | EL 5kg | 1185545 | Pant Rm 2 | 726 | 1774 | n/a | On | n/a | Y | Y | Y | Y | N | PM | Relatively new unit, low run hours. |
| 4 | ELMC 5kg | 90871 | Plant Rm 1 | 28454 | n/a | n/a | On | n/a | Y | Y | Y | Y | Y | PM | Older unit, cylinder needs replaced, leaking from inlet. |
| 5 | ELMC 5kg | 90873 | Plant Rm by Pod 6 | 19290 | n/a | n/a | On | n/a | Y | Y | Y | Y | N | PM | Older unit, in good condition. |