|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Humidifier Survey Checklist Page …… of…….** | | | | | | | | | | | | | | | |
| **Engineer** | | | | **Type of visit:** | | | | | **Date:** | | | | | **Building ref** | |
| **Item No.** | **Equipment** | **Serial number** | **Ref/ location** | **Hours** | **Service counter (next service hrs)** | **Last service date** | **Units status On/ Off** | **Fault history** | **Installation checked** | **Inspection for leaks**  **(unit off)** | **Drain valve/ pump check** | **Basic operation check** | **Parts required Y/ N** | **Works required (PM No parts/ PM parts/ repair)** | **Comments (inc parts & work)**  **(add if photo taken)** |
| 11 | ELMC 5kg | 90872 | Plant Rm 4 | 0 | n/a | n/a | On | n/a | Y | Y | N | N | Y | PM/re pair | Old unit, running hors are 0, possible PCB change. Inlet Vv failed 4.1V, 2.6K ohms. |
| 12 | SKE 10M | 07E2916644 | Plant Rm 2A | ? | n/a | n/a | On | n/a | Y | Y | Y | Y | Y | PM | Unit should be cleaned and gasket replaced. |
| 13 | SKE 5M | 07E3316762 | Plant Rm 4A | ? | n/a | n/a | Off | Over Heat | Y | Y | N | N | Y | PM | Water level sensor SKE05 SW PROBSM-ASSY Clean cylinder and replace gasket. |
| 14 | SKE 5M | 07E3316764 | Plant Rm 5A | ? | n/a | n/a | Off | n/a | Y | Y | N | N | Y | PM | Issue raised last visit, customer waiting for parts. |
| 15 | SKE 10M | 07E2916646 | Plant Rm 7A | ? | n/a | n/a | On | n/a | Y | Y | Y | Y | Y | PM | Gasket and clean |