## 5kg units
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1138156 | Mk5 5kg | DF1115497 | Upper snap ring | 1 | 2500 | 64876 | 64876 | 0 | 5000 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 64876 | 64876 | 0 | 5000 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 64876 | 64876 | 0 | 5000 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 64876 | 58811 | 6065 | 5000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 64876 | 64876 | 0 | 5000 | 0
|  | DF1115539 | Float assembly | 1 | 7500 | 64876 | 58811 | 6065 | 5000 | 1
|  | DF1115546 | Float hose | 1 | 10000 | 64876 | 64876 | 0 | 5000 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 64876 | 58811 | 6065 | 5000 | 1
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 64876 | 58811 | 6065 | 5000 | 0
|  | 1115507 | Contactor | 1 | 15000 | 64876 | 0 | 64876 | 5000 | 1
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 64876 | 0 | 64876 | 5000 | 1
|  | DF1103350 | Condensate hose | 1 | 20000 | 64876 | 0 | 64876 | 5000 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 64876 | 58811 | 6065 | 5000 | 1
|  | 1115535 | Inlet Vv | 1 | 20000 | 64876 | 0 | 64876 | 5000 | 1
|  | 1115503 | Steam Nipple | 1 | 15000 | 64876 | 0 | 64876 | 5000 | 1
|  | 1115476 | Element Single | 3 | When less than 42ohms
|  | 1115475 | Element 3pc | 1 | When less than 42ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1145224 | Mk5 5kg | DF1115497 | Upper snap ring | 1 | 2500 | 58056 | 58056 | 0 | 5000 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 58056 | 58056 | 0 | 5000 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 58056 | 58056 | 0 | 5000 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 58056 | 35370 | 22686 | 5000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 58056 | 58056 | 0 | 5000 | 0
|  | DF1115539 | Float assembly | 1 | 7500 | 58056 | 58056 | 0 | 5000 | 0
|  | DF1115546 | Float hose | 1 | 10000 | 58056 | 58056 | 0 | 5000 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 58056 | 52110 | 5946 | 5000 | 1
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 58056 | 58056 | 0 | 5000 | 0
|  | 1115503 | Steam Nipple | 1 | 15000 | 58056 | 52110 | 5946 | 5000 | 0
|  | 1115507 | Contactor | 1 | 15000 | 58056 | 46906 | 11150 | 5000 | 1
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 58056 | 31857 | 26199 | 5000 | 1
|  | DF1103350 | Condensate hose | 1 | 20000 | 58056 | 0 | 58056 | 5000 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 58056 | 35370 | 22686 | 5000 | 1
|  | 1115535 | Inlet Vv | 1 | 20000 | 58056 | 58056 | 0 | 5000 | 0
|  | 1115503 | Steam Nipple | 1 | 15000 | 58056 | 58056 | 0 | 5000 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms
|  | 1115475 | Element 3pc | 1 | When less than 42ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1145223 | Mk5 5kg | DF1115497 | Upper snap ring | 1 | 2500 | 7961 | 7961 | 0 | 300 | 0
|  | DF1115498 | Lower snap ring | 1 | 2500 | 7961 | 7961 | 0 | 300 | 0
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 7961 | 6853 | 1108 | 300 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 7961 | 6853 | 1108 | 300 | 0
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 7961 | 6853 | 1108 | 300 | 0
|  | DF1115539 | Float assembly | 1 | 7500 | 7961 | 6856 | 1105 | 300 | 0
|  | DF1115546 | Float hose | 1 | 10000 | 7961 | 0 | 7961 | 300 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 7961 | 6853 | 1108 | 300 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 7961 | 0 | 7961 | 300 | 0
|  | 1115507 | Contactor | 1 | 15000 | 7961 | 0 | 7961 | 300 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 7961 | 0 | 7961 | 300 | 0
|  | DF1103350 | Condensate hose | 1 | 20000 | 7961 | 0 | 7961 | 300 | 0
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 7961 | 6853 | 1108 | 300 | 0
|  | 1115535 | Inlet Vv | 1 | 20000 | 7961 | 0 | 7961 | 300 | 0
|  | 1115503 | Steam Nipple | 1 | 15000 | 7961 | 0 | 7961 | 300 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements

## 10kg units
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1144441 | Mk5 10kg | DF1115497 | Upper snap ring | 1 | 2500 | 22155 | 22155 | 0 | 2000 | 0
|  | DF1115498 | Lower snap ring | 1 | 2500 | 22155 | 20091 | 2064 | 2000 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 22155 | 22155 | 0 | 2000 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 22155 | 14247 | 7908 | 2000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 22155 | 14247 | 7908 | 2000 | 1
|  | DF1115539 | Float assembly | 1 | 7500 | 22155 | 22155 | 0 | 2000 | 0
|  | DF1115546 | Float hose | 1 | 10000 | 22155 | 22155 | 0 | 2000 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 22155 | 14247 | 7908 | 2000 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 22155 | 18067 | 4088 | 2000 | 0
|  | 1115507 | Contactor | 1 | 15000 | 22155 | 0 | 22155 | 2000 | 1
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 22155 | 20091 | 2064 | 2000 | 0
|  | DF1103350 | Condensate hose | 1 | 20000 | 22155 | 0 | 22155 | 2000 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 22155 | 14247 | 7908 | 2000 | 0
|  | 1115535 | Inlet Vv | 1 | 20000 | 22155 | 0 | 22155 | 2000 | 1
|  | 1115503 | Steam Nipple | 1 | 15000 | 22155 | 0 | 22155 | 2000 | 1
|  | 1115480 | Element Single | 3 | When less than 21ohms
|  | 1115479 | Element 3pc | 1 | When less than 21ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1120147 | Mk5 10kg | DF1115497 | Upper snap ring | 1 | 2500 | 54583 | 54583 | 0 | 5000 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 54583 | 54583 | 0 | 5000 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 54583 | 54583 | 0 | 5000 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 54583 | 44857 | 9726 | 5000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 54583 | 54583 | 0 | 5000 | 0
|  | DF1115539 | Float assembly | 1 | 7500 | 54583 | 49462 | 5121 | 5000 | 1
|  | DF1115546 | Float hose | 1 | 10000 | 54583 | 44857 | 9726 | 5000 | 1
|  | DF2575607 | Drain coupling | 1 | 10000 | 54583 | 49462 | 5121 | 5000 | 1
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 54583 | 54583 | 0 | 5000 | 0
|  | 1115507 | Contactor | 1 | 15000 | 54583 | 54583 | 0 | 5000 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 54583 | 0 | 54583 | 5000 | 1
|  | DF1103350 | Condensate hose | 1 | 20000 | 54583 | 0 | 54583 | 5000 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 54583 | 44857 | 9726 | 5000 | 1
|  | 1115535 | Inlet Vv | 1 | 20000 | 54583 | 0 | 54583 | 5000 | 1
|  | 1115503 | Steam Nipple | 1 | 15000 | 54583 | 49462 | 5121 | 5000 | 0
|  | 1115480 | Element Single | 3 | When less than 21ohms
|  | 1115479 | Element 3pc |  | When less than 21ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1122776 | Mk5 10kg | DF1115497 | Upper snap ring | 1 | 2500 | 42039 | 42039 | 0 | 3000 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 42039 | 42039 | 0 | 3000 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 42039 | 39034 | 3005 | 3000 | 1
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 42039 | 39034 | 3005 | 3000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 42039 | 39034 | 3005 | 3000 | 1
|  | DF1115539 | Float assembly | 1 | 7500 | 42039 | 39034 | 3005 | 3000 | 0
|  | DF1115546 | Float hose | 1 | 10000 | 42039 | 39034 | 3005 | 3000 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 42039 | 39034 | 3005 | 3000 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 42039 | 35545 | 6494 | 3000 | 0
|  | 1115507 | Contactor | 1 | 15000 | 42039 | 35545 | 6494 | 3000 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 42039 | 0 | 42039 | 3000 | 1
|  | DF1103350 | Condensate hose | 1 | 20000 | 42039 | 0 | 42039 | 3000 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 42039 | 0 | 42039 | 3000 | 1
|  | 1115535 | Inlet Vv | 1 | 20000 | 42039 | 0 | 42039 | 3000 | 1
|  | 1115503 | Steam Nipple | 1 | 15000 | 42039 | 39034 | 3005 | 3000 | 0
|  | 1115480 | Element Single | 3 | When less than 21ohms
|  | 1115479 | Element 3pc |  | When less than 21ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1144440 | Mk5 10kg | DF1115497 | Upper snap ring | 1 | 2500 | 655 | 655 | 0 | 500 | 0
|  | DF1115498 | Lower snap ring | 1 | 2500 | 655 | 655 | 0 | 500 | 0
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 655 | 655 | 0 | 500 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 655 | 655 | 0 | 500 | 0
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 655 | 0 | 655 | 500 | 0
|  | DF1115539 | Float assembly | 1 | 7500 | 655 | 0 | 655 | 500 | 0
|  | DF1115546 | Float hose | 1 | 10000 | 655 | 0 | 655 | 500 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 655 | 655 | 0 | 500 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 655 | 0 | 655 | 500 | 0
|  | 1115507 | Contactor | 1 | 15000 | 655 | 0 | 655 | 500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 655 | 0 | 655 | 500 | 0
|  | DF1103350 | Condensate hose | 1 | 20000 | 655 | 0 | 655 | 500 | 0
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 655 | 655 | 0 | 500 | 0
|  | 1115535 | Inlet Vv | 1 | 20000 | 655 | 0 | 655 | 500 | 0
|  | 1115503 | Steam Nipple | 1 | 15000 | 655 | 0 | 655 | 500 | 0
|  | 1115480 | Element Single | 3 | When less than 21ohms
|  | 1115479 | Element 3pc |  | When less than 21ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1123191 | Mk5 10kg | DF1115497 | Upper snap ring | 1 | 2500 | 54275 | 54030 | 245 | 3500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 54275 | 54030 | 245 | 3500 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 54275 | 54030 | 245 | 3500 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 54275 | 54030 | 245 | 3500 | 0
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 54275 | 54275 | 0 | 3500 | 0
|  | DF1115539 | Float assembly | 1 | 7500 | 54275 | 54030 | 245 | 3500 | 0
|  | DF1115546 | Float hose | 1 | 10000 | 54275 | 54030 | 245 | 3500 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 54275 | 54030 | 245 | 3500 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 54275 | 54030 | 245 | 3500 | 0
|  | 1115507 | Contactor | 1 | 15000 | 54275 | 54275 | 0 | 3500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 54275 | 0 | 54275 | 3500 | 1
|  | DF1103350 | Condensate hose | 1 | 20000 | 54275 | 0 | 54275 | 3500 | 1
|  | 1115535 | Inlet Vv | 1 | 20000 | 54275 | 0 | 54275 | 3500 | 1
|  | 1115503 | Steam Nipple | 1 | 15000 | 54275 | 36530 | 17745 | 3500 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 54275 | 54030 | 245 | 3500 | 0
|  | 1115480 | Element Single | 3 | When less than 21ohms
|  | 1115479 | Element 3pc |  | When less than 21ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements

## 20kg Units
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1146169 | Mk5 20kg | DF1115497 | Upper snap ring | 1 | 2500 | 31439 | 31439 | 0 | 3000 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 31439 | 31439 | 0 | 3000 | 1
|  | DF1100966 | Tank gasket 20-80 | 1 | 5000 | 31439 | 31439 | 0 | 3000 | 1
|  | DF1119796 | Collector foil 20-80 | 1 | 5000 | 31439 | 25805 | 5634 | 3000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 31439 | 25805 | 5634 | 3000 | 1
|  | DF1115539 | Float assembly | 1 | 7500 | 31439 | 25805 | 5634 | 3000 | 1
|  | DF1115546 | Float hose | 1 | 10000 | 31439 | 28835 | 2604 | 3000 | 1
|  | DF2575607 | Drain coupling | 1 | 10000 | 31439 | 28835 | 2604 | 3000 | 1
|  | DF1115500 | Scale collector 20-40kg | 1 | 15000 | 31439 | 28835 | 2604 | 3000 | 1
|  | 1115509 | 20kg Contactor | 2 | 15000 | 31439 | 0 | 31439 | 3000 | 1
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 31439 | 0 | 31439 | 3000 | 1
|  | DF1103350 | Condensate hose | 1 | 20000 | 31439 | 0 | 31439 | 3000 | 1
|  | 2557692 | 20kg Cylinder insert with foil | 1 | 10000 | 31439 | 25805 | 5634 | 3000 | 1
|  | 1104535 | Inlet Vv | 1 | 20000 | 31439 | 28835 | 2604 | 3000 | 1
|  | 1115503 | Steam Nipple | 1 | 15000 | 31439 | 31439 | 0 | 3000 | 1
|  | 1115480 | Element Single | 3 | When less than 21ohms
|  | 1115479 | Element 3pc | 1 | When less than 21ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements

## Spares Planning
Part Number | Part Name | No parts per unit | Required | Site Stock | Order on SP
DF1115497 | Upper snap ring | 1 | 6 | 6 | 0
DF1115498 | Lower snap ring | 1 | 7 | 1 | 6
DF1101516 | Tank gasket 5-16 | 1 | 1 | 0 | 1
DF1100966 | Tank gasket 20-80 | 1 | 1 | 1 | 0
1119793 | Collector foil 5-16 | 1 | 5 | 4 | 1
DF1119796 | Collector foil 20-80 | 1 | 1 | 1 | 0
DF1103817 | Steam outlet hose | 1 | 3 | 3 | 0
DF1115539 | Float assembly | 1 | 3 | 2 | 1
DF1115546 | Float hose | 1 | 2 | 0 | 2
DF2575607 | Drain coupling | 1 | 4 | 3 | 1
DF1115499 | Scale collector 5-16kg | 1 | 0 | 2 | -2
DF1115500 | Scale collector 20-40kg | 1 | 1 | 1 | 0
1115507 | 5kg - 10kg Contactor | 1 | 3 | 1 | 2
1115509 | 20kg Contactor | 2 | 1 | 0 | 2
DF1103675 | Steam hose (IDZ10 42mm) | 1 |  | 0 | 0
DF1103350 | Condensate hose | 1 |  | 0 | 0
2557691 | 5 - 16 Cylinder insert with foil | 1 | 4 | 4 | 0
2557692 | 20kg Cylinder insert with foil | 1 | 1 | 1 | 0
1115503 | Steam Nipple | 1 | 4 | 1 | 3
1115535 | 5kg - 16kg Inlet Vv | 1 | 5 | 0 | 5
1104535 | 20kg Inlet Vv | 1 | 1 | 0 | 1
1115476 | 5kg Element Single | 3 |  | 1 | -1
1115475 | 5kg Element 3pc | 1 |  | 3 | -3
1115480 | 10kg + 20kg Element Single | 3 |  | 2 | -2
1115479 | 10kg + 20kg Element 3pc | 1 |  | 1 | -1
1115532 | Pump | 1 |  | 2 | -2
1115527 | Power Board | 1 |  | 1 | -1
1115545 | Hose drain | 1 |  | 3 | -3
1119718 | Cable Harness | 1 |  | 2 | -2