## Sheet1
Unit | Model | S/N | Supply's | Location | Condition | Notes | Current Status
HygroMatik | HY1.05L | 0402078 | Zone 1 Macintosh House | Macintosh PR | Off - Faulty | Drain pump failure, leaking from cylinder to drain Pp connection. New cylinder, cylinder base, cylinder base mounting set, drain Pp, O-rings, main contactor, Inlet Vv & restrictors required | Off - Faulty
HygroMatik | HY1.05L | 0402077 | Zone 2 Macintosh House | Macintosh PR | Off - Faulty | Leaking from cylinder to drain Pp connection. New cylinder, O-rings and main contactor required. | Off - Faulty
HygroMatik | HY1.05L | 0402079 | Zone 3 Macintosh House | Macintosh PR | Off - Faulty | Drain pump failure, leaking from cylinder to drain Pp connection. New cylinder, cylinder base, cylinder base mounting set, drain Pp, O-rings, main contactor, Inlet Vv & restrictors required | Off - Faulty
HygroMatik | HY1.05L | 0402080 | Zone 4 Macintosh House | Macintosh PR | Off - Faulty | Drain pump missing from unit, along with all O-rings, mountings and drain hose set. Alsothe door lock has part of a key snapped off in it, so the unit door will not stay closed, which is an elecrical safety risk. New cylinder, cylinder base, cylinder base mounting set, drain Pp, O-rings, main contactor, Inlet Vv & restrictors and door lock required. | Off - Faulty
DriSteam | HT-12 | N498-02-01 | ? | Macintosh PR | Off - Faulty | Exessive fill time fault, drain Vv is passing, causing the fill time out fault to shut down unit. Valve, ½" SST ball 505000-003 | Off - Faulty
HygroMatik | HY2 17 | 0402081 | Gallery East 1 | Main Gallery PR | Off | Fills, drains, Cylinder fault, low conductivity, even though cylinder is thick with scale. No hose adapter or clip. New cylinder, gaskets, Adapter for steam hose and securing clip. | On steaming - Cylinder fault
HygroMatik | HY2 17 | 0402083 | Gallery East 2 | Main Gallery PR | Off | Fills, drains, Cylinder fault, low conductivity, even though cylinder is thick with scale. No hose adapter or clip. New cylinder, gaskets, Adapter for steam hose and securing clip. | On steaming - Cylinder fault
HygroMatik | HY12-C | 1203121 | ? | Main Gallery PR | Off | Fills, drains, runs. Cylinder fault, low conductivity, even though cylinder is thick with scale. New cylinder, gaskets. | On steaming - Cylinder fault
HygroMatik | HY1.08L | 03A 4701 | Zone C+D | Main Gallery PR | Off | Fills, drains, runs. New cylinder, gaskets. | On steaming - Cylinder fault
HygroMatik | HY1.08L | 03A 4699 | Zone E | Main Gallery PR | Off | Fills, drains, does not run. Cylinder does not stop filling. New cylinder, gaskets. | Off - Faulty
HygroMatik | HY1.08L | 03A 4700 | Zone A+B | Main Gallery PR | Off | Drain pump failure, leaking from cylinder to drain Pp connection. New cylinder, cylinder base, cylinder base mounting set, drain Pp, O-rings, main contactor, Inlet Vv & restrictors, all hoses required | Off - Faulty