## UOG assets
Status | Item No. | Building Ref | Building Description | Location Ref | Location Description | ID | Surveyors Desc | Technology | Manufacturer | Model | S/N | Size/Capacity | EST. Year Installed | Postcode
Condair contract expired, awaiting renewal | 1 | 100 | JAMES WATT NANOFABRICATION CENTRE | 1000351 | PLANT ROOM (ELECTRICAL) | HUM | humidifier No 4A | electrode | Electrovap | ELMC 10 | 95127 | 10kg/h | 2005 | G12 8QQ
| 2 | 100 | JAMES WATT NANOFABRICATION CENTRE | 1000351 | PLANT ROOM (ELECTRICAL) | HUM | humidifier No 4B | electrode | Electrovap | ELMC 45 | 94921 | 45kg/h | 2005 | G12 8QQ
| 3 | 100 | JAMES WATT NANOFABRICATION CENTRE | 1000351 | PLANT ROOM (ELECTRICAL) | HUM | humidifier no 2A | electrode | Electrovap | ELMC 45 | 94921 | 45kg/h | 2005 | G12 8QQ
| 4 | 100 | JAMES WATT NANOFABRICATION CENTRE | 1000351 | PLANT ROOM (ELECTRICAL) | HUM | humidifier no 2B | electrode | Electrovap | ELMC 60 | 94956 | 60kg/h | 2005 | G12 8QQ
| 5 | 100 | JAMES WATT NANOFABRICATION CENTRE | 1000351 | PLANT ROOM (ELECTRICAL) | HUM | humidifier No 5A | electrode | Electrovap | ELMC 90 | 95195 | 90kg/h | 2005 | G12 8QQ
| 6 | 100 | JAMES WATT NANOFABRICATION CENTRE | 1000351 | PLANT ROOM (ELECTRICAL) | HUM | humidifier 3A | electrode | Condair | CP3-90 | 1145024 | 90kg/h | 2005 | G12 8QQ
| 7 | 100 | JAMES WATT NANOFABRICATION CENTRE | 1000351 | PLANT ROOM (ELECTRICAL) | HUM | humidifier 1A | electrode | Electrovap | ELMC 60 | 94958 | 60kg/h | 2005 | G12 8QQ
| 8 | 100 | JAMES WATT NANOFABRICATION CENTRE | 1000351 | PLANT ROOM (ELECTRICAL) | HUM | humidifier 1B | electrode | Electrovap | ELMC 45 | 94922 | 45kg/h | 2005 | G12 8QQ
| 9 | 102 | JAMES WATT BUILDING | 1020348 | PLANT ROOM | HUM | Humidifier | Resistive | Electrovap | RTH 15LC | 11663 | 104kg/h | 2018 | G12 8QQ
| 10 | 102 | JAMES WATT BUILDING | 1020348 | PLANT ROOM | HUM | Humidifier | Resistive | Electrovap | RTH 7LC | 11662 | 104kg/h | 2018 | G12 8QQ
Not found | 11 | 124 | JOSEPH BLACK BUILDING | 124B225G | PLANT ROOM (MECHANICAL) | HUM | Humidifier | electrode | Electrovap | ELMC 10 | 91334 | 10kg/hr | 2010 | G12 8QQ
| 12 | 124 | JOSEPH BLACK BUILDING | 124B204 | CIRCULATION AREA | HUM | Humidifier | TBC | Hygromatik | FLH09 | N/A | 10kg/hr | 2010 | G12 8QQ
No access | 13 | 124 | JOSEPH BLACK BUILDING | 124B211B | INSECT ROOM | HUM | Humidifier | TBC | Hygromatik | FLH09 | N/A | 10kg/hr | 2010 | G12 8QQ
Not found | 14 | 124 | JOSEPH BLACK BUILDING | 124B212A | ACADEMIC STORE | HUM | Humidifier | TBC | Hygromatik | FLH09 | N/A | 10kg/hr | 2010 | G12 8QQ
No access | 15 | 124 | JOSEPH BLACK BUILDING | 124B213 | INSECT ROOM | HUM | Humidifier | TBC | Hygromatik | FLH09 | N/A | 10kg/hr | 2010 | G12 8QQ
Unfound | 16 | 124 | JOSEPH BLACK BUILDING | 124B214 | RESEARCH LAB-BENCHED | HUM | humidifier | TBC | Carel | N/A | N/A | 10kg/hr | 2010 | G12 8QQ
| 17 | 124 | JOSEPH BLACK BUILDING | 124B229 | PLANT ROOM (MECHANICAL) | HUM | humidifier | Resistive | Hygromatik | FLH09 | N/A | 10kg/hr | 2010 | G12 8QQ
Twin unit |  | 124 | JOSEPH BLACK BUILDING | 124B229 | PLANT ROOM (MECHANICAL) | HUM | humidifier |  | Hygromatik | FLH09 | N/A | 10kg/hr | 2010 | G12 8QQ
| 18 | 124 | JOSEPH BLACK BUILDING | 124B229 | PLANT ROOM (MECHANICAL) | HUM | humidifier | Resistive | Hygromatik | FLH09 | N/A | 10kg/hr | 2010 | G12 8QQ
Twin unit |  | 124 | JOSEPH BLACK BUILDING | 124B229 | PLANT ROOM (MECHANICAL) | HUM | humidifier |  | Hygromatik | FLH09 | N/A | 10kg/hr | 2010 | G12 8QQ
| 21 | 126 | DAVIDSON BUILDING | 1260113 | MICROSCOPY LAB | HUM | humidifier | TBC | TBC | CSS241R/99 | FF81744320-001 | TBC |  | G12 8QQ
| 22 | 126 | DAVIDSON BUILDING | 1260113 | MICROSCOPY LAB | HUM | humidifier | TBC | TBC | CSS241R/99 | FF81744320-002 | TBC |  | G12 8QQ
| 23 | 134 | CENTRAL RESEARCH FACILITY | 1340400E | PLANTROOM (MECHANICAL) | HUM | Humidifier | electrode | Hygromatik | HY116-C | 1700025 | 116KG/HR | 2018 | G12 8QQ
| 24 | 134 | CENTRAL RESEARCH FACILITY | 1340400E | PLANTROOM (MECHANICAL) | HUM | Humidifier | electrode | Hygromatik | HY116-C | 1700021 | 116KG/HR | 2018 | G12 8QQ
| 25 | 134 | CENTRAL RESEARCH FACILITY | 1340400E | PLANTROOM (MECHANICAL) | HUM | Humidifier | electrode | Hygromatik | HY116-C | 1700022 | 116KG/HR | 2018 | G12 8QQ
| 26 | 170 | WOLFSON MEDICAL SCHOOL BUILDING | 1700119 | PLANT ROOM (MECHANICAL) | HUM | Seminar/communications room AHU Calorifier | electrode | ElectroVap | ELMC60 | 90069 | 60kg/hr | 2004 | G12 8QQ
| 27 | 170 | WOLFSON MEDICAL SCHOOL BUILDING | 1700514 | PLANT ROOM (ELECT/MECH) | HUM | AHU 2 humidifier | electrode | Electrovap | ELMC90 | 90038 | 60kg/hr | 2004 | G12 8QQ
| 28 | 170 | WOLFSON MEDICAL SCHOOL BUILDING | 1700514 | PLANT ROOM (ELECT/MECH) | HUM | AHU 3 humidifier | electrode | Electrovap | ELMC90 | 90030 | 90kg/hr | 2004 | G12 8QQ
Removed | 29 | 203 | RANKINE BUILDING | 2030220 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | TBC | Spirax Sarco | DB282EM | 9023335 | TBC | 2005 | G12 8LT
| 30 | 323 | SAUGHFIELD BUILDING (DATA CENTRE) | 3230203 | ROOFTOP PLANT AREA | HUM | Humidifer AHU2 | electrode | Condair | EL5 | 1218756 | 5kg/hr | 2019 | TBC
Duplicate | 32 | 323 | SAUGHFIELD BUILDING (DATA CENTRE) | 3230203 | ROOFTOP PLANT AREA | HUM | Humidifer AHU2 | electrode | Condair | EL5 | 1218756 | 5kg/hr | 2019 | TBC
| 31 | 323 | SAUGHFIELD BUILDING (DATA CENTRE) | 3230204 | RISER | HUM | Humidifer AHU1 | electrode | Condair | EL5 | 1213406 | 5kg/hr | 2019 | TBC
Duplicate | 33 | 323 | SAUGHFIELD BUILDING (DATA CENTRE) | 3230204 | RISER | HUM | Humidifer AHU1 | electrode | Condair | EL5 | 1213406 | 5kg/hr | 2019 | TBC
| 34 | 324 | HUNTERIAN ART GALLERY | 3240110 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | Resistive | DriSteem | HT-12 | N498-02-01 | 15kg/hr | 1974 ? | G12 8QQ
| 35 | 326 | LIBRARY | 3260122 | NON-ACADEMIC STORE | HUM | Steam Humidifier | Resistive | Carel | heaterSteam | N/A | 60kg/hr | 2011 | G12 8QE
| 36 | 326 | LIBRARY | 3260230 | PLANT ROOM (MECHANICAL) | HUM | Humidifier for AHU 2 | electrode | Vapac | WL30 | V04482 | 415V 3 PH - 30KG/HR | 2011 | G12 8QE
| 37 | 326 | LIBRARY | 3260236 | CONSERVATION | HUM | Steam heater system for humidification | Resistive | Carel | heaterSteam | N/A | 60kg/hr | 2011 | G12 8QE
| 38 | 326 | LIBRARY | 3260346 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | Resistive | Vapac | LR60PD | V51890 | 60kg/h | 2011 | G12 8QE
| 39 | 326 | LIBRARY | 3260430A | Plant Room Entrance | HUM | Mains Tap Off | electrode | Vapac | WL60 | V09572 | 60kg/hr | 2011 | G12 8QE
| 40 | 326 | LIBRARY | 3260521A | PLANT ROOM (MECHANICAL) | HUM | AHU Humidifier | electrode | Vapac | WL30 | V10061 | 30kg/h | 2011 | G12 8QE
| 41 | 326 | LIBRARY | 3260628 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | electrode | Vapac | LE60 | v22601 | 60kg/hr | 2011 | G12 8QE
| 42 | 326 | LIBRARY | 3260726 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | TBC | VAPAC | LE3U | V22602 | 30kg/h | 2011 | G12 8QE
| 43 | 326 | LIBRARY | 3260826 | PLANT ROOM (MECHANICAL) | HUM | HUM unit | electrode | Vapac | LE60 | V25958 | 60kg/hr | 2011 | G12 8QE
| 44 | 326 | LIBRARY | 3260925 | PLANT ROOM (ELECTRICAL) | HUM | Humidifier | electrode | Vapac | LE30 | V25943 | 30kg/h | 2011 | G12 8QE
| 45 | 326 | LIBRARY | 3261028 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | electrode | Vapac | LE-60 | V29375 | 60kg/hr | 2011 | G12 8QE
| 46 | 326 | LIBRARY | 3261037 | ACCESS TO ROOF SPACE OVER LEVEL 9 ANNEX BLOCK | HUM | AHU | Resistive | Condair | RS-OC20 | 1218970 | 20kg/hr | 2011 | G12 8QE
| 47 | 326 | LIBRARY | 3261037 | ACCESS TO ROOF SPACE OVER LEVEL 9 ANNEX BLOCK | HUM | AHU | Resistive | Condair | RS-OC20 | 1218971 | 20kg/hr | 2011 | G12 8QE
| 48 | 326 | LIBRARY | 3261124 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | electrode | VAPAC | LE30 | V29374 | 30kg/h | 2011 | G12 8QE
| 49 | 326 | LIBRARY | 3261233 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | resistive | Condair | RS10 | 1218974 | 30kg/h | 2018 | G12 8QE
| 50 | 326 | LIBRARY | 3261233 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | resistive | Condair | RS10 | 1218973 | 30kg/h | 2018 | G12 8QE
| 51 | 326 | LIBRARY | 3261233 | PLANT ROOM (MECHANICAL) | HUM | Humidifier | resistive | Condair | RS10 | 1218972 | 30kg/h | 2018 | G12 8QE
| 52 | 327 | CCNI-CENTRE FOR COGNITIVE NEUROIMAGING | 3270107 | CHAIR STORE | HUM | Humidifier | Evaporative | Condair | EL 5kg | 07E3116689 | 5kg/hr | ? | ?
| 53 | 505 | THURSO STREET 13 | 5050408 | PLANT ROOM (MECHANICAL) | HUM | humidifier | TBC | Vapac |  | V35377 | TBC |  | G116PE
| 54 | 505 | THURSO STREET 13 | 5050501D | CIRCULATION AREA | HUM | humidifier | TBC | Vapac |  | 39806 | TBC |  | G116PE
| 55 | 706 | VET RESEARCH FACILITY-EXTENSION BLOCK | 7060403 | PLANT ROOM (MECHANICAL) | HUM | Humidifier. | Resistive | Condair | RS120 | 1200629 | 120kg/hr |  | G61 1BD
| 56 | 706 | VET RESEARCH FACILITY-EXTENSION BLOCK | 7060403 | PLANT ROOM (MECHANICAL) | HUM | Humidifier. | Resistive | Condair | RS120 | 1200629 | 120kg/hr |  | G61 1BD
| 57 | 706 | VET RESEARCH FACILITY-EXTENSION BLOCK | 7060403 | PLANT ROOM (MECHANICAL) | HUM | Humidifier. | Resistive | Condair | RS120 | 1200629 | 120kg/hr |  | G61 1BD
| 58 | 706 | VET RESEARCH FACILITY - OLD BLOCK |  | PLANT ROOM (MECHANICAL) | HUM | Humidifier |  | Condair
| 59 | 706 | VET RESEARCH FACILITY- OLD BLOCK |  | PLANT ROOM (MECHANICAL) | HUM | Humidifier |  | Condair
Only 2 in plant room. | 60 | 706 | VET RESEARCH FACILITY- OLD BLOCK |  | PLANT ROOM (MECHANICAL) | HUM | Humidifier |  | Condair
| 61 | 636 | SMALL ANIMAL HOSPITAL |  | PLANT ROOM (MECHANICAL) | HUM | Humidifier |  | Condair
| 62 | 636 | SMALL ANIMAL HOSPITAL |  | PLANT ROOM (MECHANICAL) | HUM | Humidifier |  | Condair
| 63 | 636 | SMALL ANIMAL HOSPITAL |  | PLANT ROOM (MECHANICAL) | HUM | Humidifier |  | Condair
Not found | 64 |  | TAY HOUSE - 300 BATH STREET - LEVEL 6 | T010629 | CONFERENCE ROOM | HUM | Humidifier | Resistive | SKE neptonic | SFSKE50M400 J3 | 09E2819806 | 50kg/hr |  | G2 4LH
Not found | 65 | T01 | TAY HOUSE - 300 BATH STREET - LEVEL 6 | T010629 | CONFERENCE ROOM | HUM | Humidifier | Resistive | SKE neptonic | SFSE50M400 J3 | 09e2819810 | 50kg/hr |  | G2 4LH
| 66 | 718 | JARRETT |  | INSECTARY | HUM | Humidifier |  | SKE Neptonic |  |  |  |  | G61 1QH
| 67 | 718 | JARRETT |  | INSECTARY | HUM | Humidifier |  | SKE Neptonic |  |  |  |  | G61 1QH
| 68 | 718 | JARRETT |  | INSECTARY | HUM | Humidifier
| 69 | 718 | JARRETT |  | INSECTARY | HUM | Humidifier
| 70 | 719 | HENRY WELLCOME |  | INSECTARY | HUM | Humidifier
| 71 | 719 | HENRY WELLCOME |  | INSECTARY | HUM | Humidifier
| 72 | 719 | HENRY WELLCOME |  | INSECTARY | HUM | Humidifier
| 73 | 719 | HENRY WELLCOME |  | INSECTARY | HUM | Humidifier
Not found | 74 | ? | HENRY WELLCOME |  | INSECTARY | HUM | Humidifier
Site contact not aware of unit | 75 |  | Bio chemistry department |  |  |  |  | electrode | ElectroVap Humidifier | ELMC60 | TBC | 60kg/hr |  | G12 8QR
Site contact not aware of unit | 76 | [6 empty] | electrode | ElectroVap Humidifier | ELMC60 | TBC | 60kg/hr |  | G12 8QR
Site contact not aware of unit | 77 | [6 empty] | electrode | ElectroVap Humidifier | ELMC90 | TBC | 90kg/hr |  | G12 8QR
| 78 |  | Weipers equine |  |  |  |  | electrode | ElectroVap Humidifier | EL2S 90 | TBC | 90kg/hr |  | G61 1QH
| 79 | [6 empty] | electrode | ElectroVap Humidifier | EL2S 90 | TBC | 90kg/hr |  | G61 1QH
Site contact not aware of unit | 80 |  | Kelvin data centre |  |  |  |  | electrode | EL Basic 5kg/hr 400v | EL5210004 | 1213406 | 5kg/hr |  | G12 8AD
Site contact not aware of unit | 81 | [6 empty] | electrode | EL Basic 5kg/hr 400v | EL5210004 | 1218756 | 5kg/hr |  | G12 8AD
Site contact not aware of unit | 82 |  | Stevenson building |  |  |  |  | electrode | EL Basic 5kg/hr 230v | EL5210001 | 1221781 | 5kg/hr |  | G12 8LT
Site contact not aware of unit | 83 |  | Research Hub |  |  |  |  | Cold water evaporative | ME Module 2550mmWx3500mmH | ME-CL2550S-3500-F75 | 1230952 | TBC |  | G12 8QQ
Site contact not aware of unit | 84 | [6 empty] | Cold water evaporative | ME Module 2700mmWx3500mmH | ME-CL2700S-3500-F75 | 1230925 | TBC |  | G12 8QQ
Newly commissioned | 85 | 725 | Gemric building |  | PLANT ROOM (MECHANICAL) | HUM | Humidifier |  | Condair |  |  |  |  | G61 1 QH

## Survey
Humidifier Survey Checklist Page …… of…….
Item No. | Equipment | Technology | Obsolescence | Serial number | Ref/ location | Hours | Service counter (next service hrs) | Last service date | Units status On/ Off | Fault history | Installation checked | Inspection for leaks (unit off) | Drain valve/ pump check | Basic operation check | Parts required Y/ N | Parts | ADNO Commetns | Replacement unit costs | Budget install | budget parts | labour costs | Comments (inc parts & work)
Building ref: Joseph Black 124
12 | Carel humiSteam | Electrode |  | 19216 | Insectary Main Corridor | ? | Due | ? | On | ? | Y | Y | Y | Y | Y | Cylinder | Have not seen since survey |  |  | 400 |  | Unit needs new cylinder. Don’t think unit is getting to setpoint, 70rh displayed. Unit warm but not hot enough to steam. Further investigation required.
17 | HygroMatik HL 90-C | Resistive |  | 1600834 1600836 | Mechanical Plant Rm | 10720 | ? | ? | On | ? | Y | Y | Y | Y | N? | Cylinders & PCB | Have not seen since survey |  |  | 852 |  | 2 Units combined, a 30kg and a 60kg according to manufacturer label information. (Cylinders are the same size visually) 2 Photos Software only recognises 1 cylinder at 30kg, yet both cylinders heat when humidifying. Possible software programming issue. Software version 1.21 Further investigation required.
18 | HygroMatik HL 90-C | Resistive |  | 1600831 1600833 | Mechanical Plant Rm | 12176 | ? | ? | On | ? | Y | Y | Y | Y | N? | Cylinders & PCB | Have not seen since survey |  |  | 852 | 544 | ""
Building ref: Davidson 126
21 | Airedale ? | Electrode |  | ? | Rm 113 | ? | ? | ? | Off | ? | N | N | N | N | ? |  | Close control unit, not supported |  |  | ??? |  | I have no idea what type of unit this is, could not get covers off, think a small step ladder is required to gain access. Further investigation required.
22 | Airedale ? |  |  | ? | Rm 113 | ? | ? | ? | On | ? | N | N | N | N | ? |  | Close control unit, not supported |  |  |  |  | ""
Building ref: CENTRAL RESEARCH FACILITY 134
23 | HygroMatik HY 116-C | Electrode |  | 1700025 | Plant Rm | 1063 | ? | ? | Off | ? | Y | Y | Y | N | Y | cylinder/ drain pump | Have not seen since survey |  |  | 2962 |  | 1 of 2 cylinders fill and drain, could not test operation. New cylinders required. Further investigation required.
24 | HygroMatik HY 116-C | Electrode |  | 1700021 | Plant Rm | 1888 | ? | ? | Off | ? | Y | Y | Y | N | Y | cylinder/ drain pump | Have not seen since survey |  |  | 2962 |  | 1 of 2 cylinders fill and drain, could not test operation. New cylinders required. Further investigation required.
25 | HygroMatik HY 116-C | Electrode |  | 1700022 | Plant Rm | 4242 | ? | ? | Off | ? | Y | Y | Y | N | Y | cylinder/ drain pump | Have not seen since survey |  |  | 2962 | 544 | 1 of 2 cylinders fill and drain, could not test operation. New cylinders required. Further investigation required.
Building ref: WOLFSON MEDICAL SCHOOL BUILDING 170
27 | ElectroVap ELMC 90kg | Electrode |  | 90038 | 5th Floor Plant Rm | 0? | ? | ? | Off | ? | Y | Y | Y | N | Y | Replace | Have not seen since survey | 10993.5 |  |  |  | Very bad state. Photo's taken. Installation degraded. Minimum parts 3 cylinders, inlet Vv's drain Pps
28 | ElectroVap ELMC 60kg | Electrode |  | 90030 | 5th Floor Plant Rm | 0? | ? | ? | Off | ? | Y | Y | Y | N | Y | Replace | Have not seen since survey | 8610.5 |  |  |  | Bad state. Photo's taken. Installation degraded. Minimum parts 3 cylinders, inlet Vv's drain Pps
26 | ElectroVap ELMC 60kg | Electrode |  | 90069 | Basement Car park Plant Rm | 17203 | ? | ? | Off | ? | Y | Y | Y | N | Y | Replace | Have not seen since survey | 8610.5 | 8013 |  |  | Bad state. Photo's taken. Installation degraded. Minimum parts 3 cylinders, inlet Vv's drain Pps
Building ref: SAUGHFIELD BUILDING (DATA CENTRE) 323
31 | Condair EL 5kg | Electrode |  | 1213406 | AHU 1 Data centre Plant Rm | 153.8 | Due | None | On | Fill time out Current time out | Y | Y | Y | N | Y | No parts | Still low running hour, newer units. |  |  | 95 |  | Supply water issues causing units to be in fault, site contact suggested problem with supply. Will need to investigate with site to identify cause of fault.
32 | Condair EL 5kg | Electrode |  | 1218756 | AHU 2 Data centre Roof space | 82.5 | Due | None | On | Current time out | Y | Y | Y | N | Y | No parts | Still low running hour, newer units. |  |  | 95 | 404 | ""
Building ref: HUNTERIAN ART GALLERY 324
34 | Dristeem HT 12 | Resistive |  | N498-02-01 | Mackintosh Plant Rm | ? | ? | ? | Off | Excessive fill time | Y | Y | Y | N | Y | repair investigation | Have not seen since survey |  |  | 821 |  | Drain does not appear to be working. Auto drain and flush pending message. 1 Photo. Further investigation required.
Not on list | HygroMatik HY1 0.5-L | Electrode |  | 0402078 | Mackintosh Plant Rm | ? | ? | ? | Off | ? | Y | Y | Y | N | Y | Cylinder | Have not seen since survey |  |  | 441 |  | Cylinder required. Further investigation required.
Not on list | HygroMatik HY1 0.5-L | Electrode |  | 0402077 | Mackintosh Plant Rm | ? | ? | ? | On | ? | Y | Y | Y | N | Y | Cylinder | Have not seen since survey |  |  | 441 |  | Cylinder required. Further investigation required.
Not on list | HygroMatik HY1 0.5-L | Electrode |  | 0402079 | Mackintosh Plant Rm | ? | ? | ? | On | ? | Y | Y | Y | N | Y | Cylinder | Have not seen since survey |  |  | 441 |  | Cylinder required. Further investigation required.
Not on list | HygroMatik HY1 0.5-L | Electrode |  | 0402080 | Mackintosh Plant Rm | ? | ? | ? | Off | ? | Y | Y | Y | N | Y | cylinder/ drain pump | Have not seen since survey |  |  | 618 | 544 | New drain pump and Cylinder required. Further investigation required.
Not on list | HygroMatik HY2 17EMP | Electrode |  | 0402081 | Main Gallery Plant Rm | 1253.17 | ? | ? | Off | ? | Y | Y | Y | N | Y | Cylinder | Have not seen since survey |  |  | 763 |  | 1 Photo Cylinder required. Further investigation required.
Not on list | HygroMatik HY2 17EMP | Electrode |  | 0402083 | Main Gallery Plant Rm | 1122 | ? | ? | Off | ? | Y | Y | Y | N | Y | Cylinder | Have not seen since survey |  |  | 763 |  | Cylinder required. Further investigation required.
Not on list | HygroMatik HY 17-C | Electrode |  | 1203121 | Main Gallery Plant Rm | 1995 | ? | ? | On | ? | Y | Y | Y | Y | Y | Cylinder | Have not seen since survey |  |  | 763 |  | Cylinder required. Further investigation required.
Not on list | HygroMatik HY1 0.8L | Electrode |  | 03A5699 | Main Gallery Plant Rm | ? | ? | ? | On | ? | Y | Y | Y | N | Y | Cylinder | Have not seen since survey |  |  | 441 |  | Cylinder required. Further investigation required.
Not on list | HygroMatik HY1 0.8L | Electrode |  | 03A4701 | Main Gallery Plant Rm | ? | ? | ? | Off | ? | Y | Y | Y | N | Y | Cylinder | Have not seen since survey |  |  | 441 | 544 | Cylinder required. Further investigation required.
Building ref: Library 326
Not on list | Condair RS 8kg | Resistive |  | 1218975 | Non Academic Store Floor 1 | 4611 | Due | None | On | None | Y | Y | Y | Y | Y | DF1115497 RS2599191 1100966 DF1119796 RS2579820 | Have not seen since survey |  |  | 391 |  | Unit in good condition. Parts as per 5k hours running.
35 | Carel heaterSteam 60kg | Resistive |  | A00026806 | Mechanical Plant Rm Floor 1 | ? | ? | ? | Off | ? | Y | Y | Y | Y | N | Investigation Xplus | Have not seen since survey |  |  |  |  | Unit appears to be operational. Will require first PM to fully asses parts required.
36 | Vapac WL30 | Electrode | Yes | V04482 | Mechanical Plant Rm Floor 2 | ? | ? | ? | Off | ? | Y | Y | Y | Y | Y | Replace | Have not seen since survey | 5641.75 |  |  |  | 1 Photo. Cylinder and drain pump required. Further investigation required.
37 | Carel heaterSteam | Resistive |  | A00026745 | Conservation | 5.2 | ? | ? | On | ? | Y | Y | Y | Y | Y/? | Investigation Xplus | Have not seen since survey |  |  |  | 544 | Unit in fault, fault codes EA, EL, EE Further investigation required.
38 | Vapac LR60PD | Resistive |  | V51890 | Mechanical Plant Rm Floor 3 | ? | ? | ? | Off | ? | Y | Y | N | N | Y | Replace | Have not seen since survey | 8990 |  |  |  | 1 Photo. No wires to inlet Vv below unit (photo). Cylinder, inlet Vv and inlet Vv cables required. Unit does not get past initializing on display. Further investigation required.
39 | Vapac WL60 | Electrode | Yes | VO9572 | Mechanical Plant Rm Floor 4 | 1182 | ? | ? | Off | ? | Y | Y | Y | Y | Y | Replace | Have not seen since survey | 8610.5 |  |  |  | 1 Photo. Cylinder, drain pump and inlet Vv required. Does not fill. Further investigation required.
40 | Vapac WL30 | Electrode | Yes | V10061 | Mechanical Plant Rm Floor 5 | 212 | ? | ? | Off | ? | Y | Y | Y | N | Y | Replace | Have not seen since survey | 5641.75 |  |  |  | 1 Photo. Cylinder required. Unit does not fill. Further investigation required.
41 | Vapac LE60 | Electrode |  | V22601 | Mechanical Plant Rm Floor 6 | ? | ? | ? | Off | ? | Y | Y | Y | N | Y | Cylinder / drain PCB / display | Have not seen since survey |  |  | 900 | 544 | LCD not responding. Cylinder and drain pump required. Unit does not fill. Further investigation required.
42 | Vapac LE30 | Electrode |  | V22602 | Mechanical Plant Rm Floor 7 | ? | ? | ? | Off | ? | Y | Y | N | N | Y | Replace | Have not seen since survey | 5641.75 | 10163 |  |  | 2 Photo's. Cylinder and cable harness required. Unit does not respond, electrode cable melted. Unit does not fill. Further investigation required.
43 | Vapac LE60 | Electrode |  | V25958 | Mechanical Plant Rm Floor 8 | ? | ? | ? | Off | ? | Y | Y | N | N | Y | ? | Have not seen since survey |  |  |  |  | 1 Photo. Cylinder and control card required. LED and switches not responding. Unit does not fill. Further investigation required.
44 | Vapac LE30 | Electrode |  | V25943 | Mechanical Plant Rm Floor 9 | ? | ? | ? | Off | ? | Y | Y | N | N | Y | ? | Have not seen since survey |  |  |  |  | Cylinder required. Unit not showing power, however power is available. Further investigation required.
45 | Vapac LE60 | Electrode |  | V29375 | Mechanical Plant Rm Floor 10 | ? | ? | ? | Off | ? | Y | Y | Y | N | Y | ? | Have not seen since survey |  |  |  | 544 | 1 Photo. Cylinders and fill/drain cup required. Unit does not fill. Unit stuck on initializing. Further investigation required.
46 | Condair RS 20kg | Resistive |  | 1218970 | Roof space Floor 10 | 1757 | 1300 | None | On | None | Y | Y | Y | Y | N | ? | Have not seen since survey |  |  | 81 |  | Good condition.
47 | Condair RS 20kg | Resistive |  | 1218971 | Roof space Floor 10 | 48 | 2950 | None | On | None | Y | Y | Y | Y | N | ? | Have not seen since survey |  |  | 81 |  | Good condition.
48 | Vapac LE30 | Electrode |  | V29374 | Mechanical Plant Rm Floor 11 | ? | ? | ? | Off | ? | Y | Y | Y | Y | Y | Cylinder | Have not seen since survey |  |  | 343 |  | Cylinder required. Other parts on first PM visit.
49 | Condair RS 10kg | Resistive |  | 1218974 | Mechanical Plant Rm Floor 12 | 5188 | Due | None | On | Level void Max drain time | Y | Y | N | N | Y | DF1115497 RS2599191 1100966 DF1119796 RS2579820 | Have not seen since survey |  |  | 468 | 544 | Unit in fault. Parts as per 5k running hours. Unit in 100% demand, but not filling correctly, resulting in faults. Possible inlet Vv, float assembly or software issue.
50 | Condair RS 10kg | Resistive |  | 1218973 | Mechanical Plant Rm Floor 12 | 3731 | Due | None | On | None | Y | Y | Y | Y | Y | DF1115497 RS2599191 1100966 DF1119796 RS2579820 | Have not seen since survey |  |  | 391 |  | Parts as per 4k running hours.
51 | Condair RS 30kg | Resistive |  | 1218972 | Mechanical Plant Rm Floor 12 | 3649 | Due | None | On | None | Y | Y | Y | Y | Y | DF1115497 RS2599191 1100966 DF1119796 RS2579820 | Have not seen since survey |  |  | 393 |  | Parts as per 4k running hours.
Building ref: CCNI-CENTRE FOR COGNITIVE NEUROIMAGING 327
52 | Condair EL 5kg | Electrode |  | 1221781 | MRI | 0 | 3000 | None | On | None | Y | Y | Y | N | N | ? | Have not seen since survey |  |  |  | 404 | Unit does not appear to have been commissioned, no log book, no hours run would indicate no control voltage.
Building ref: Thurso Street 505
53 | Vapac LE18D | Electrode |  | V35377 | Mechanical Plant Rm Level 3 | 13366 454 | Due | ? | Off | 35 drain faults 3 feed faults | Y | Y | Y | N | Y | ? | Have not seen since survey |  |  |  |  | Cylinder required. Not sure why left off, appears to work.
54 | Vapac LE18D | Electrode |  | V39806 | Mechanical Plant Rm Level 4 | 2072 16 | Due | ? | Off | ? | Y | Y | Y | N | Y | ? | Have not seen since survey |  |  |  | 404 | Unit not responding. LED flash red green for 2 seconds, fault as per manual. Further investigation required.
Building ref: VET RESEARCH FACILITY 706
58 | Condair RS 30kg | Resistive |  | 1217383 | Old Block Plant Rm | 8953 | Due | None | On | Max drain time 20/03/20 Max fill 08/19 | Y | Y | Y | Y | Y |  | Worth popping in to check parts for service |  |  | 393 | 544 | Parts as per 9k running hours.
59 | Condair RS 30kg | Resistive |  | 1217384 | Old Block Plant Rm | 9146 | Due | None | On | None | Y | Y | Y | Y | Y |  | Worth popping in to check parts for service |  |  | 486 |  | Parts as per 10k running hours.
60 | Condair RS 40kg | Resistive |  | 1200629 | Extension Block Plant Rm | 12407 | Due | By SC 07/10/19 | On | Max fill time 10/09/20 | Y | Y | Y | Y | Y |  | Worth popping in to check parts for service |  |  | 393 |  | Parts as per 6k running hours. Part of 120kg unit split into 3 separate 40kg units on last Condair visit in Sept 19.
61 | Condair RS 40kg | Resistive |  | 1200629 | Extension Block Plant Rm | 7916 | Due | By SC 07/10/19 | On | Level void Max drain time Heating voltage missing All 01/09/20 | Y | Y | Y | N | Y |  | Worth popping in to check parts for service |  |  | 393 |  | Parts as per 8k running hours. Part of 120kg unit split into 3 separate 40kg units on last Condair visit in Sept 19. Unit in fault. Further investigation required.
62 | Condair RS 40kg | Resistive |  | 1200629 | Extension Block Plant Rm | 6182 | Due | By SC 07/10/19 | On | Max fill time Consistent since 01/20 | Y | Y | Y | N | Y |  | Worth popping in to check parts for service |  |  | 393 | 404 | Parts as per 6k running hours. Part of 120kg unit split into 3 separate 40kg units on last Condair visit in Sept 19. Unit leaking from cylinder gasket, over filling. Float assembly required. Unit left off. Further investigation required.
Building ref: Small animal hospital
61 | Condair RS 40kg | Resistive |  | 0? | Plant RM | 356 | 2700 | None | Off | None | Y | Y | Y | Y | Y | Investigate | Have not seen since survey |  |  |  | 544 | Issues from commissioning, date time etc No serial number in software. Unit off on arrival, no reason given.
62 | Condair RS 40kg | Resistive |  | 1218492 | Plant RM | 229 | 2800 | None | Off | Driver missing 08/01/20 | Y | Y | Y | Y | Y | ? | Have not seen since survey |  |  |  |  | Driver issues fault. Unit off on arrival, no reason given.
63 | Condair RS 40kg | Resistive |  | 1218492 | Plant RM | 157 | 2850 | None | Off | Driver missing 01/10/10 | Y | Y | Y | Y | Y | ? | Have not seen since survey |  |  |  |  | Driver issues fault. Unit off on arrival, no reason given.
Not on list | Condair RS 80kg | Resistive |  | 1218491 | Plant RM | 1298 | 1300 | None | Off | None | Y | Y | Y | Y | Y | ? | Have not seen since survey |  |  |  |  | Unit off on arrival, no reason given.
Building ref: Jarret 718
66 | SKE SF-SKE05M-230-1 | Resistive |  | 18E0134117 | Insectary | 1474 | ? | ? | On | ? | Y | Y | Y | Y | N | PM | Worth popping in to check parts for service |  |  |  | 544 | Unit alternates with Item No. 67. Asses parts required on first PM.
67 | SKE SF-SKE05M-230-1 | Resistive |  | 18E2334979 | Insectary | 8822 | ? | ? | On | ? | Y | Y | Y | Y | N | PM | Worth popping in to check parts for service |  |  | 10 |  | Unit alternates with Item No. 66. Asses parts required on first PM.
68 | SKE SF-SKE05M-230-1 | Resistive |  | 18E0134126 | Insectary | 1457 | ? | ? | On | ? | Y | Y | Y | Y | N | PM | Worth popping in to check parts for service |  |  | 10 |  | Unit alternates with Item No. 69, site have had issues with drops in humidity on changeover. Asses parts required on first PM.
69 | SKE SF-SKE05M-230-1 | Resistive |  | 18E0134127 | Insectary | 1496 | ? | ? | On | ? | Y | Y | Y | Y | N | PM | Worth popping in to check parts for service |  |  | 10 |  | Unit alternates with Item No. 68, site have had issues with drops in humidity on changeover. Asses parts required on first PM.
Building ref: HENRY WELLCOME 719
70 | Condair EL 10kg | Electrode |  | 1177107 | Insectary | 3125.2 | Due | None | On | None | Y | Y | Y | Y | N | ? | Worth popping in to check parts for service |  |  | 143 | 544 | Cylinder installed 09/19.
71 | HygroMatik C10-C | Electrode |  | 1601328 | Insectary | 3319 | ? | ? | On | ? | Y | Y | Y | Y | N | ? | Worth popping in to check parts for service |  |  | 441 |  | Cylinder installed 09/19.
72 | HygroMatik C06-C | Electrode |  | 1603355 | Insectary | 6996 | ? | ? | On | ? | Y | Y | Y | Y | Y | ? | Worth popping in to check parts for service |  |  | 441 |  | Cylinder required.
73 | HygroMatik C06-C | Electrode |  | 1603356 | Insectary | 4723 | ? | ? | On | ? | Y | Y | Y | Y | N | ? | Worth popping in to check parts for service |  |  | 441 |  | Cylinder installed 08/19.
Building ref: Weipers equine 708
78 | Electrovap EL 25-90 | Electrode | Yes | 80162 | Upstairs Plant Rm Surgery space | ? | ? | ? | Off | ? | Y | N | N | N | Y | Beond repair | Have not seen since survey | 10993.5 |  |  |  | 1 Photo. Unit in very poor condition. Will require a lot of work to make operational, if even possible. No power to unit. Further investigation required.
79 | Electrovap EL 25-90 | Electrode | yes | 80163 | Upstairs Plant Rm Surgery space | ? | ? | ? | Off | ? | Y | N | N | N | Y | Beond repair | Have not seen since survey | 10993.5 | 6813 |  |  | 1 Photo. Unit in very poor condition. Will require a lot of work to make operational, if even possible. No power to unit. Further investigation required.
[18 empty] | 84727.25 | 14826 | 23715 | 7740 | 131008.25
| Key |  |  |  |  | ? ?: Totals
| Operational unit requires PM/PM+parts |  |  |  |  | ? ?: 19
| Unit is operational or non operational and requires repair/Investigation |  |  |  |  | ? ?: 37
| Non operational unit, requires substantial work |  |  |  |  | ? ?: 7
[6 empty] | Units | 63
Please note
Parts costs are list prices excluding VAT & Delivery. . Prices are budget at this stage. Confirmation of these prices will be supplied within a detailed quotation on request
Equipment costs exclude delivery VAT & commissioning

## Water quality
Post code | Mean conductivity | Zone
G12 8QQ | 53.2 | Milngavie M3
G12 8QE | 53.2 | Milngavie M3
G11 6PE | 54.77 | Milngavie M4
G61 1BD | 51.86 | Milngavie M1
G2 4LH | 53.2 | Milngavie M3
Conductivity ranges | Electrode
Condair | 125-1250
Low conductivity cylinder | <125
Hygromatik | 125-1250
Low conductivity cylinder | ???
Vapac | 80-1000
Low conductivity cylinder | 80-200

## Install scope of works
Installation & Commissioning
Clients scope of works:
· Provide a suitable power supply for the heating circuit of each humidifier. This should be terminated at a rotary isolator within 1m of the humidifier location. Ensure power supply is fused correctly.
· Provide a suitable 230V 10A power supply for the control circuit of each humidifier. This should be terminated at an isolator within 1m of the humidifier location. (This is not applicable if the CVI/TR option is selected)
· Provide a suitable 230V 10A power supply for the RO unit. This should be terminated at an isolator within 1m of the RO location
· Provide suitable water and drain connections within one meter of proposed humidifier/RO location(s).
Connect BMS interface signal wiring or provide identifiable control BMS interface wiring to be connected by us.
· Provide a suitable competent person for electrical isolation at your distribution board.
· Provide access/lifting equipment if required.
· Disposal of any redundant equipment and packaging.
All services shall be provided in accordance with the instructions within the installation and operating manual.
Condair scope of works:
Removal of the existing humidification equipment:
· Safe disconnection of electrical power supply
· Isolate existing water supply, and disconnect pipe work.
· Disconnect drain.
· Remove the existing humidifiers.
· Remove the existing steam distribution lances and blank off aperture if necessary.
· Remove interconnecting steam pipe work and insulation.
· Lay aside redundant equipment in nominated location for disposal by others.
Installation of new Condair humidification equipment:
· Deliver to site.
· Mount steam humidifiers in their designated, pre-agreed location. Where necessary construct bespoke slotted channel framework.
· Install steam lances within the ventilation system and suitably fix or mount fan distribution unit above the humidifier.
· Install interconnecting steam pipe work between humidifier and steam distribution lances / fan distribution unit. Suitably fix and insulate as required.
· Connect humidifier drain outlets to main site drain, modifying where necessary.
· Install steam lance condensate pipework back to main drain.
· Pipe from isolated mains water supply humidifiers in 15mm copper tubing and suitably support.
· Wire from isolated electrical supplies to humidifier main heating and controls circuits.
· Mount sensor and high limit humidistats in agreed locations in accordance with the Condair manual.
· Connect identifiable BMS interface cabling to humidifiers.
· Fully commission the unit, demonstrate and hand over.
Equipment links
Condair RS