## Sheet1
Pressure regulator
Unit | Serial number | Total Hours | Feb Hours | July Hours | Aug Hours | Last Pump change | Cartredge filters changed | Filter 5 micron 20" | O-ring for water filter | Sterile breather filter 0,2 my | UV 10W | UV Quarts | Feb RO | July RO | Aug RO | Print frame relay Pump and On/Off valve | Contactor | Service kit for PAHT 2 | Service kit coupling PAHT 2/4 | Repair kit for one valve; core, spring, o-rings | Repair kit for one valve; guide tube, core, spring, o-rings | Service kit | On/off valve rep kit 1/2" 10 bar_24V | Check valve 1/4" | Nozzle ML 4.5 Stainless | Nozzle ML 2,5 Stainless Changed | Nozzle ML 2,5 Stainless Need Changed
AHU 7 | 2015058 2417506 | 23093 | 3282 | 2292 | 25504 | SK 11492 | Y | Next visit | Next visit | Next visit | Next visit | Next Visit | 645l/h, 75uS | 900l/h, 35uS | 900l/h, 35uS | Next visit | Next Visit | New Pump | Next Visit | Next Visit | Next Visit | Next visit | Next Visit | 2022-09-01 | N/A | 0 | 0
AHU 3 | 2015053 2417500 | 24203 | 3227 | 3076 | 27434 | SK 10867 | Y | Next visit | Next visit | Next visit | Next visit | Next Visit | 211l/h, 5uS | 227l/h, 4.7uS | 227l/h, 4.7uS | Next visit | Next Visit | New Pump | Next Visit | Next Visit | Next Visit | Next visit | Next Visit | 2022-09-01 | N/A | 0 | 0
AHU 2 | 2015057 2417507 | 4293 | 149 | 4382 | 4403 | None | Y | Next visit | Next visit | Next visit | Next visit | Next Visit | 450L/H 5.4uS | 553l/h, 4.5uS | 553l/h, 4.5uS | Next visit | Next Visit | Service kit for PAHT 2 | Next Visit | Next Visit | Next Visit | Next visit | Next Visit | 2022-09-01 | N/A | 0 | 0
AHU 8 | 2015052 2417509 | 6658 | 81 | 6807 | 6828 | None | Y | Next visit | Next visit | Next visit | Next visit | Next Visit | 450l/h, 4uS | 514l/h, 3.5uS | 514l/h, 3.5uS | Next visit | Next Visit | Service kit for PAHT 2 | Next Visit | Next Visit | Next Visit | Next visit | Next Visit | 2022-09-01 | N/A | 0 | 2
AHU 9 | 2015055 2417508 | 9548 | 145 | 9697 | 9781 | None | Y | Next visit | Next visit | Next visit | Next visit | Next Visit | 423l/h, 3uS | 450lh, 2.7uS | 450lh, 2.7uS | Next visit | Next Visit | Service kit for PAHT 2 | Next Visit | Next Visit | Next Visit | Next visit | Next Visit | 2022-09-01 | N/A | 0 | 0
AHU 6 | 2015059 | 12349 | 3306 | 15490 | 15563 | SK 6199 | Y | Next visit | Next visit | Next visit | Next visit | Next Visit | 378l/h, 4.5uS | 514l/h, 7uS | 514l/h, 7uS | Next visit | Next Visit | Service kit for PAHT 2 | Next Visit | Next Visit | Next Visit | Next visit | Next Visit | 2022-09-01 | N/A | 0 | 5
AHU 5 | 2015054 2417501 | 17769 | 150 | 17919 | 17938 | SK 10721 | Y | Next visit | Next visit | Next visit | Next visit | Next Visit | 600/h, 22uS | 720l/h, 16 | 720l/h, 16uS | Next visit | Next Visit | Service kit for PAHT 2 | Next Visit | Next Visit | Next Visit | Next visit | Next Visit | 2022-09-01 | N/A | 0 | 2
AHU 1 | 2015060 2417502 | 9495 | 140 | 9645 | 9666 | None | Y | Next visit | Next visit | Next visit | Next visit | Next Visit | 327l/h, 7uS | 400l/h, 7 | 400l/h, 7uS | Next visit | Next Visit | Service kit for PAHT 2 | Next Visit | Next Visit | Next Visit | Next visit | Next Visit | 2022-09-01 | N/A | 0 | 0
AHU 4 | 2015056 2417503 | 4354 | 122 | 4504 | 4524 | None | Y | Next visit | Next visit | Next visit | Next visit | Next Visit | 300l/h, 2.2uS | 480l/h, 3.5 | 480l/h, 3.5uS | Next visit | Next Visit | Service kit for PAHT 2 | Next Visit | Next Visit | Next Visit | Next visit | Next Visit | 2022-09-01 | N/A | 0 | 8
Site stock