## Mk5
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
114824 | Mk5 8kg | DF1115497 | Upper snap ring | 2 | 2500 | 0 |  | 0 |  | 0
|  | DF1115498 | Lower snap ring | 2 | 2500 | 0 |  | 0 | 1000 | 0
|  | DF1100966 | Tank gasket 20-80 | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF1119796 | Collector foil 20-80 | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF1103817 | Steam outlet hose | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF1115539 | Float assembly | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF1115546 | Float hose | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF2575607 | Drain coupling | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 0 |  | 0 | 1000 | 0
|  | 1115507 | 30A Contactor | 3 | 10000 | 0 |  | 0 | 1000 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 0 |  | 0 | 1000 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 0 |  | 0 | 1000 | 0
|  | 1115490 | 16-40 Cylinder insert with grid | 2 | 10000 | 0 |  | 0 | 1000 | 0
|  | 1115535 | Inlet Vv | 2 | 10000 | 0 |  | 0 | 1000 | 0
|  | 1115503 | Steam Nipple | 2 | 10000 | 0 |  | 0 | 1000 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms
|  | 1115475 | Element 3pc | 1 | When less than 42ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
114825 | Mk5 50kg | DF1115497 | Upper snap ring | 2 | 2500 | 13152 |  | 13152 | 1000 | 2
|  | DF1115498 | Lower snap ring | 2 | 2500 | 13152 |  | 13152 | 1000 | 2
|  | DF1100966 | Tank gasket 20-80 | 2 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | DF1119796 | Collector foil 20-80 | 2 | 5000 | 13152 |  | 13152 | 1000 | 2
|  | DF1103817 | Steam outlet hose | 2 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | DF1115539 | Float assembly | 2 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | DF1115546 | Float hose | 2 | 5000 | 13152 |  | 13152 | 1000 | 2
|  | DF2575607 | Drain coupling | 2 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | 1115507 | 30A Contactor | 3 | 10000 | 13152 |  | 13152 | 1000 | 3
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 13152 |  | 13152 | 1000 | 1
|  | DF1103350 | Condensate hose | 1 | 10000 | 13152 |  | 13152 | 1000 | 1
|  | 1115490 | 16-40 Cylinder insert with grid | 2 | 10000 | 13152 |  | 13152 | 1000 | 2
|  | 1115535 | Inlet Vv | 2 | 10000 | 13152 |  | 13152 | 1000 | 2
|  | 1115503 | Steam Nipple | 2 | 10000 | 13152 |  | 13152 | 1000 | 2
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
|  | 1115511 | 50A Contactor | 1 | 10000 | 13152 |  | 13152 | 1000 | 1
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1143823 | Mk5 50kg | DF1115497 | Upper snap ring | 2 | 2500 | 4808 |  | 4808 | 800 | 2
|  | DF1115498 | Lower snap ring | 2 | 2500 | 4808 |  | 4808 | 800 | 2
|  | DF1100966 | Tank gasket 20-80 | 2 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | DF1119796 | Collector foil 20-80 | 2 | 5000 | 4808 |  | 4808 | 800 | 2
|  | DF1103817 | Steam outlet hose | 2 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | DF1115539 | Float assembly | 2 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | DF1115546 | Float hose | 2 | 5000 | 4808 |  | 4808 | 800 | 2
|  | DF2575607 | Drain coupling | 2 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | 1115509 | 30A Contactor | 3 | 10000 | 4808 |  | 4808 | 800 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 4808 |  | 4808 | 800 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 4808 |  | 4808 | 800 | 0
|  | 1115490 | 16-40 Cylinder insert with grid | 2 | 10000 | 4808 |  | 4808 | 800 | 0
|  | 1115535 | Inlet Vv | 2 | 10000 | 4808 |  | 4808 | 800 | 0
|  | 1115503 | Steam Nipple | 2 | 10000 | 4808 |  | 4808 | 800 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
|  | 1115511 | 50A Contactor | 1 | 10000 | 4808 |  | 4808 | 800 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1143821 | Mk5 30kg | DF1115497 | Upper snap ring | 1 | 2500 | 7056 |  | 7056 | 1500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 7056 |  | 7056 | 1500 | 1
|  | DF1100966 | Tank gasket 20-80 | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | DF1119796 | Collector foil 20-80 | 1 | 5000 | 7056 |  | 7056 | 1500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 7056 |  | 7056 | 1500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | 1115511 | 50A Contactor | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | 1115490 | 16-40 Cylinder insert with grid | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | 1115535 | Inlet Vv | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | 1115503 | Steam Nipple | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
|  | 1115509 | 30A Contactor | 2 | 10000 | 7056 |  | 7056 | 1500 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1143820 | Mk5 24kg | DF1115497 | Upper snap ring | 1 | 2500 | 8495 |  | 8495 | 1000 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 8495 |  | 8495 | 1000 | 1
|  | DF1100966 | Tank gasket 20-80 | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | DF1119796 | Collector foil 20-80 | 1 | 5000 | 8495 |  | 8495 | 1000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 8495 |  | 8495 | 1000 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | 1115511 | 50A Contactor | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | 1115490 | 16-40 Cylinder insert with grid | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | 1115535 | Inlet Vv | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | 1115503 | Steam Nipple | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
|  | 1115509 | 30A Contactor | 2 | 10000 | 8495 |  | 8495 | 1000 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1148717 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 15342 |  | 15342 | 1500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 15342 | 11983 | 3359 | 1500 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 15342 |  | 15342 | 1500 | 1
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 15342 |  | 15342 | 1500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 15342 | 11983 | 3359 | 1500 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 15342 | 11983 | 3359 | 1500 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 15342 |  | 15342 | 1500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 15342 | 11983 | 3359 | 1500 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 15342 | 11983 | 3359 | 1500 | 0
|  | 1115507 | 25 AContactor | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | DF1103350 | Condensate hose | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | 1115535 | Inlet Vv | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | 1115503 | Steam Nipple | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1448713 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 13226 |  | 13226 | 2500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 13226 |  | 13226 | 2500 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 13226 | 8999 | 4227 | 2500 | 1
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 13226 |  | 13226 | 2500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 13226 | 8999 | 4227 | 2500 | 1
|  | DF1115539 | Float assembly | 1 | 5000 | 13226 | 8999 | 4227 | 2500 | 1
|  | DF1115546 | Float hose | 1 | 5000 | 13226 |  | 13226 | 2500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 13226 |  | 13226 | 2500 | 1
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 13226 | 8999 | 4227 | 2500 | 1
|  | 1115507 | 25 AContactor | 1 | 10000 | 13226 | 8999 | 4227 | 2500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | DF1103350 | Condensate hose | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | 1115535 | Inlet Vv | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | 1115503 | Steam Nipple | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1448714 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 6531 |  | 6531 | 500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 6531 |  | 6531 | 500 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 6531 |  | 6531 | 500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 6531 |  | 6531 | 500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | 1115507 | 25 AContactor | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | 1115535 | Inlet Vv | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | 1115503 | Steam Nipple | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1148715 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 17972 |  | 17972 | 3000 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 17972 |  | 17972 | 3000 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 17972 |  | 17972 | 3000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | DF1115539 | Float assembly | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | DF1115546 | Float hose | 1 | 5000 | 17972 |  | 17972 | 3000 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | 1115507 | 25 AContactor | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | DF1103350 | Condensate hose | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | 1115535 | Inlet Vv | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | 1115503 | Steam Nipple | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1148716 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 7564 |  | 7564 | 500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 7564 |  | 7564 | 500 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 7564 |  | 7564 | 500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 7564 |  | 7564 | 500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | 1115507 | 25 AContactor | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | 1115535 | Inlet Vv | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | 1115503 | Steam Nipple | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms
|  | 1115475 | Element 3pc | 1 | When less than 42ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements

## Mk5 Spares Planning
Unit | Part Number | Part Name | No parts per unit | Site Spares | Required | SP
Mk5 | DF1115497 | Upper snap ring | 1 | 23 | 11 | -12
| DF1115498 | Lower snap ring | 1 | 0 | 11 | 11
| DF1101516 | Tank gasket 5-16 | 1 | 4 | 0 | -4
| 1119793 | Collector foil 5-16 | 1 | 0 | 0 | 0
| DF1103817 | Steam outlet hose | 1 | 3 | 2 | -1
| DF1115539 | Float assembly | 1 | 15 | 2 | -13
| DF1115546 | Float hose | 1 | 0 | 11 | 11
| DF2575607 | Drain coupling | 1 | 11 | 2 | -9
| DF1115499 | Scale collector 5-16kg | 1 | 5 | 2 | -3
| 1115507 | Contactor | 1 | 0 | 2 | 2
| DF1103675 | Steam hose (IDZ10 42mm) | 1 | 0 | 4 | 4
| DF1103350 | Condensate hose | 1 | 0 | 4 | 4
| 1115489 | 5 - 16 Cylinder insert with grid | 1 | 5 | 3 | -2
| 1115535 | Inlet Vv | 1 | 0 | 5 | 5
| 1115503 | Steam Nipple | 1 | 0 | 5 | 5
| 1115476 | Element Single | 3 |  |  | 0
| 1115475 | Element 3pc | 1 |  |  | 0
| DF2560304 | Element gaskets | 1 |  |  | 0
| 1115500 | Scale collector 20-40kg | 1 | 6 | 0 | -6
| 1115490 | 16-40 Cylinder insert with grid | 1 | 6 | 2 | -4
| DF1119796 | Collector foil 20-80 | 1 | 0 | 6 | 6
| DF1100966 | Tank gasket 20-80 | 1 | 6 | 0 | -6
| 1115509 | Contactor 30A | 1 | 1 | 3 | 2
| 1115511 | Contactor 50A | 1 | 0 | 1 | 1