## Mk5
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
114824 | Mk5 8kg | DF1115497 | Upper snap ring | 2 | 2500 | 0 |  | 0 |  | 0
|  | DF1115498 | Lower snap ring | 2 | 2500 | 0 |  | 0 | 1000 | 0
|  | DF1100966 | Tank gasket 20-80 | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF1119796 | Collector foil 20-80 | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF1103817 | Steam outlet hose | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF1115539 | Float assembly | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF1115546 | Float hose | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | DF2575607 | Drain coupling | 2 | 5000 | 0 |  | 0 | 1000 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 0 |  | 0 | 1000 | 0
|  | 1115507 | 30A Contactor | 3 | 10000 | 0 |  | 0 | 1000 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 0 |  | 0 | 1000 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 0 |  | 0 | 1000 | 0
|  | 1115490 | 16-40 Cylinder insert with grid | 2 | 10000 | 0 |  | 0 | 1000 | 0
|  | 1115535 | Inlet Vv | 2 | 10000 | 0 |  | 0 | 1000 | 0
|  | 1115503 | Steam Nipple | 2 | 10000 | 0 |  | 0 | 1000 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms
|  | 1115475 | Element 3pc | 1 | When less than 42ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
114825 | Mk5 50kg | DF1115497 | Upper snap ring | 2 | 2500 | 13152 |  | 13152 | 1000 | 2
|  | DF1115498 | Lower snap ring | 2 | 2500 | 13152 |  | 13152 | 1000 | 2
|  | DF1100966 | Tank gasket 20-80 | 2 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | DF1119796 | Collector foil 20-80 | 2 | 5000 | 13152 |  | 13152 | 1000 | 2
|  | DF1103817 | Steam outlet hose | 2 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | DF1115539 | Float assembly | 2 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | DF1115546 | Float hose | 2 | 5000 | 13152 |  | 13152 | 1000 | 2
|  | DF2575607 | Drain coupling | 2 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 13152 | 11106 | 2046 | 1000 | 0
|  | 1115507 | 30A Contactor | 3 | 10000 | 13152 |  | 13152 | 1000 | 3
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 13152 |  | 13152 | 1000 | 1
|  | DF1103350 | Condensate hose | 1 | 10000 | 13152 |  | 13152 | 1000 | 1
|  | 1115490 | 16-40 Cylinder insert with grid | 2 | 10000 | 13152 |  | 13152 | 1000 | 2
|  | 1115535 | Inlet Vv | 2 | 10000 | 13152 |  | 13152 | 1000 | 2
|  | 1115503 | Steam Nipple | 2 | 10000 | 13152 |  | 13152 | 1000 | 2
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
|  | 1115511 | 50A Contactor | 1 | 10000 | 13152 |  | 13152 | 1000 | 1
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1143823 | Mk5 50kg | DF1115497 | Upper snap ring | 2 | 2500 | 4808 |  | 4808 | 800 | 2
|  | DF1115498 | Lower snap ring | 2 | 2500 | 4808 |  | 4808 | 800 | 2
|  | DF1100966 | Tank gasket 20-80 | 2 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | DF1119796 | Collector foil 20-80 | 2 | 5000 | 4808 |  | 4808 | 800 | 2
|  | DF1103817 | Steam outlet hose | 2 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | DF1115539 | Float assembly | 2 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | DF1115546 | Float hose | 2 | 5000 | 4808 |  | 4808 | 800 | 2
|  | DF2575607 | Drain coupling | 2 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 4808 | 3275 | 1533 | 800 | 0
|  | 1115509 | 30A Contactor | 3 | 10000 | 4808 |  | 4808 | 800 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 4808 |  | 4808 | 800 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 4808 |  | 4808 | 800 | 0
|  | 1115490 | 16-40 Cylinder insert with grid | 2 | 10000 | 4808 |  | 4808 | 800 | 0
|  | 1115535 | Inlet Vv | 2 | 10000 | 4808 |  | 4808 | 800 | 0
|  | 1115503 | Steam Nipple | 2 | 10000 | 4808 |  | 4808 | 800 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
|  | 1115511 | 50A Contactor | 1 | 10000 | 4808 |  | 4808 | 800 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1143821 | Mk5 30kg | DF1115497 | Upper snap ring | 1 | 2500 | 7056 |  | 7056 | 1500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 7056 |  | 7056 | 1500 | 1
|  | DF1100966 | Tank gasket 20-80 | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | DF1119796 | Collector foil 20-80 | 1 | 5000 | 7056 |  | 7056 | 1500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 7056 |  | 7056 | 1500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 7056 | 4693 | 2363 | 1500 | 0
|  | 1115511 | 50A Contactor | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | 1115490 | 16-40 Cylinder insert with grid | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | 1115535 | Inlet Vv | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | 1115503 | Steam Nipple | 1 | 10000 | 7056 |  | 7056 | 1500 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
|  | 1115509 | 30A Contactor | 2 | 10000 | 7056 |  | 7056 | 1500 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1143820 | Mk5 24kg | DF1115497 | Upper snap ring | 1 | 2500 | 8495 |  | 8495 | 1000 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 8495 |  | 8495 | 1000 | 1
|  | DF1100966 | Tank gasket 20-80 | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | DF1119796 | Collector foil 20-80 | 1 | 5000 | 8495 |  | 8495 | 1000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 8495 |  | 8495 | 1000 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | 1115500 | Scale collector 20-40kg | 1 | 5000 | 8495 | 6677 | 1818 | 1000 | 0
|  | 1115511 | 50A Contactor | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | 1115490 | 16-40 Cylinder insert with grid | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | 1115535 | Inlet Vv | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | 1115503 | Steam Nipple | 1 | 10000 | 8495 |  | 8495 | 1000 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
|  | 1115509 | 30A Contactor | 2 | 10000 | 8495 |  | 8495 | 1000 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1148717 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 15342 |  | 15342 | 1500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 15342 | 11983 | 3359 | 1500 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 15342 |  | 15342 | 1500 | 1
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 15342 |  | 15342 | 1500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 15342 | 11983 | 3359 | 1500 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 15342 | 11983 | 3359 | 1500 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 15342 |  | 15342 | 1500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 15342 | 11983 | 3359 | 1500 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 15342 | 11983 | 3359 | 1500 | 0
|  | 1115507 | 25 AContactor | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | DF1103350 | Condensate hose | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | 1115535 | Inlet Vv | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | 1115503 | Steam Nipple | 1 | 10000 | 15342 |  | 15342 | 1500 | 1
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1448713 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 13226 |  | 13226 | 2500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 13226 |  | 13226 | 2500 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 13226 | 8999 | 4227 | 2500 | 1
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 13226 |  | 13226 | 2500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 13226 | 8999 | 4227 | 2500 | 1
|  | DF1115539 | Float assembly | 1 | 5000 | 13226 | 8999 | 4227 | 2500 | 1
|  | DF1115546 | Float hose | 1 | 5000 | 13226 |  | 13226 | 2500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 13226 |  | 13226 | 2500 | 1
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 13226 | 8999 | 4227 | 2500 | 1
|  | 1115507 | 25 AContactor | 1 | 10000 | 13226 | 8999 | 4227 | 2500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | DF1103350 | Condensate hose | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | 1115535 | Inlet Vv | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | 1115503 | Steam Nipple | 1 | 10000 | 13226 |  | 13226 | 2500 | 1
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1448714 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 6531 |  | 6531 | 500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 6531 |  | 6531 | 500 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 6531 |  | 6531 | 500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 6531 |  | 6531 | 500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 6531 | 6471 | 60 | 500 | 0
|  | 1115507 | 25 AContactor | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | 1115535 | Inlet Vv | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | 1115503 | Steam Nipple | 1 | 10000 | 6531 |  | 6531 | 500 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1148715 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 17972 |  | 17972 | 3000 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 17972 |  | 17972 | 3000 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 17972 |  | 17972 | 3000 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | DF1115539 | Float assembly | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | DF1115546 | Float hose | 1 | 5000 | 17972 |  | 17972 | 3000 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 17972 | 12867 | 5105 | 3000 | 1
|  | 1115507 | 25 AContactor | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | DF1103350 | Condensate hose | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | 1115535 | Inlet Vv | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | 1115503 | Steam Nipple | 1 | 10000 | 17972 |  | 17972 | 3000 | 1
|  | 1115476 | Element Single | 3 | When less than 42ohms |  |  |  |  | 0
|  | 1115475 | Element 3pc | 1 | When less than 42ohms |  |  |  |  | 0
|  | DF2560304 | Element gaskets | 1 | When changing Elements |  |  |  |  | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1148716 | Mk5 8kg | DF1115497 | Upper snap ring | 1 | 2500 | 7564 |  | 7564 | 500 | 1
|  | DF1115498 | Lower snap ring | 1 | 2500 | 7564 |  | 7564 | 500 | 1
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 7564 |  | 7564 | 500 | 1
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | DF1115539 | Float assembly | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | DF1115546 | Float hose | 1 | 5000 | 7564 |  | 7564 | 500 | 1
|  | DF2575607 | Drain coupling | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 5000 | 7564 | 7422 | 142 | 500 | 0
|  | 1115507 | 25 AContactor | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | DF1103350 | Condensate hose | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | 1115535 | Inlet Vv | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | 1115503 | Steam Nipple | 1 | 10000 | 7564 |  | 7564 | 500 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms
|  | 1115475 | Element 3pc | 1 | When less than 42ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements

## RS Units
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1192420 | RS 80kg | DF1115497 | Snap ring large | 2 | 2500 | 433 |  | 433 | 1000 | 0
|  | RS2599191 | Sealing set for tank | 2 | 2500 | 433 |  | 433 | 1000 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 2 | 5000 | 433 |  | 433 | 1000 | 0
|  | 1100966 | Tank gasket 16-40 | 2 | 5000 | 433 |  | 433 | 1000 | 0
|  | DF1119796 | Collector foil 16-40 | 2 | 20000 | 433 |  | 433 | 1000 | 0
|  | RS2579820 | Steam outlet hose | 2 | 5000 | 433 |  | 433 | 1000 | 0
|  | RS2579882 | Float assembly | 2 | 10000 | 433 |  | 433 | 1000 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 2 | 20000 | 433 |  | 433 | 1000 | 0
|  | RS2579893 | Steam hose nipple | 2 | 10000 | 433 |  | 433 | 1000 | 0
|  | 2579875 | Inlet Vv 16-40 | 2 | 20000 | 433 |  | 433 | 1000 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 2 | 10000 | 433 |  | 433 | 1000 | 0
|  | 2579884 | Water cup cpl. | 2 | 20000 | 433 |  | 433 | 1000 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 2 | 20000 | 433 |  | 433 | 1000 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 2 | 20000 | 433 |  | 433 | 1000 | 0
|  | 1117502 | Main Contactor 80A | 2 | 10000 | 433 |  | 433 | 1000 | 0
|  | 1115511 | Secondary Contactor 50A | 4 | 10000 | 433 |  | 433 | 1000 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1192418 | RS 50kg | DF1115497 | Snap ring large | 2 | 2500 | 1493 |  | 1493 | 1100 | 2
|  | RS2599191 | Sealing set for tank | 2 | 2500 | 1493 |  | 1493 | 1100 | 2
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 2 | 5000 | 1493 |  | 1493 | 1100 | 0
|  | 1100966 | Tank gasket 16-40 | 2 | 5000 | 1493 |  | 1493 | 1100 | 0
|  | DF1119796 | Collector foil 16-40 | 2 | 20000 | 1493 |  | 1493 | 1100 | 0
|  | RS2579820 | Steam outlet hose | 2 | 5000 | 1493 |  | 1493 | 1100 | 0
|  | RS2579882 | Float assembly | 2 | 10000 | 1493 |  | 1493 | 1100 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 2 | 20000 | 1493 |  | 1493 | 1100 | 0
|  | RS2579893 | Steam hose nipple | 2 | 10000 | 1493 |  | 1493 | 1100 | 0
|  | 2579875 | Inlet Vv 16-40 | 2 | 20000 | 1493 |  | 1493 | 1100 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 2 | 10000 | 1493 |  | 1493 | 1100 | 0
|  | 2579884 | Water cup cpl. | 2 | 20000 | 1493 |  | 1493 | 1100 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 2 | 20000 | 1493 |  | 1493 | 1100 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 2 | 20000 | 1493 |  | 1493 | 1100 | 0
|  | 1115511 | Main Contactor 50A | 1 | 10000 | 1493 |  | 1493 | 1100 | 0
|  | 1115509 | Secondary Contactor 32A | 4 | 10000 | 1493 |  | 1493 | 1100 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1192419 | RS 50kg | DF1115497 | Snap ring large | 2 | 2500 | 3021 |  | 3021 | 2000 | 2
|  | RS2599191 | Sealing set for tank | 2 | 2500 | 3021 |  | 3021 | 2000 | 2
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 2 | 5000 | 3021 |  | 3021 | 2000 | 2
|  | 1100966 | Tank gasket 16-40 | 2 | 5000 | 3021 |  | 3021 | 2000 | 2
|  | DF1119796 | Collector foil 16-40 | 2 | 20000 | 3021 |  | 3021 | 2000 | 0
|  | RS2579820 | Steam outlet hose | 2 | 5000 | 3021 |  | 3021 | 2000 | 2
|  | RS2579882 | Float assembly | 2 | 10000 | 3021 |  | 3021 | 2000 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 2 | 20000 | 3021 |  | 3021 | 2000 | 0
|  | RS2579893 | Steam hose nipple | 2 | 10000 | 3021 |  | 3021 | 2000 | 0
|  | 2579875 | Inlet Vv 16-40 | 2 | 20000 | 3021 |  | 3021 | 2000 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 2 | 10000 | 3021 |  | 3021 | 2000 | 0
|  | 2579884 | Water cup cpl. | 2 | 20000 | 3021 |  | 3021 | 2000 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 2 | 20000 | 3021 |  | 3021 | 2000 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 2 | 20000 | 3021 |  | 3021 | 2000 | 0
|  | 1115511 | Main Contactor 50A | 1 | 10000 | 3021 |  | 3021 | 2000 | 0
|  | 1115509 | Secondary Contactor 32A | 4 | 10000 | 3021 |  | 3021 | 2000 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1192421 | RS 80kg | DF1115497 | Snap ring large | 2 | 2500 | 219 |  | 219 | 500 | 0
|  | RS2599191 | Sealing set for tank | 2 | 2500 | 219 |  | 219 | 500 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 2 | 5000 | 219 |  | 219 | 500 | 0
|  | 1100966 | Tank gasket 16-40 | 2 | 5000 | 219 |  | 219 | 500 | 0
|  | DF1119796 | Collector foil 16-40 | 2 | 20000 | 219 |  | 219 | 500 | 0
|  | RS2579820 | Steam outlet hose | 2 | 5000 | 219 |  | 219 | 500 | 0
|  | RS2579882 | Float assembly | 2 | 10000 | 219 |  | 219 | 500 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 2 | 20000 | 219 |  | 219 | 500 | 0
|  | RS2579893 | Steam hose nipple | 2 | 10000 | 219 |  | 219 | 500 | 0
|  | 2579875 | Inlet Vv 16-40 | 2 | 20000 | 219 |  | 219 | 500 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 2 | 10000 | 219 |  | 219 | 500 | 0
|  | 2579884 | Water cup cpl. | 2 | 20000 | 219 |  | 219 | 500 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 2 | 20000 | 219 |  | 219 | 500 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 2 | 20000 | 219 |  | 219 | 500 | 0
|  | 1117502 | Main Contactor 80A | 2 | 10000 | 219 |  | 219 | 500 | 0
|  | 1115511 | Secondary Contactor 50A | 4 | 10000 | 219 |  | 219 | 500 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1192417 | RS 5-10kg | DF1115497 | Snap ring large | 1 | 2500 | 2573 |  | 2573 | 1500 | 1
|  | RS2599191 | Sealing set for tank | 1 | 2500 | 2573 |  | 2573 | 1500 | 1
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 5000 | 2573 |  | 2573 | 1500 | 0
|  | DF1101516 | Tank gasket 5-10 | 1 | 5000 | 2573 |  | 2573 | 1500 | 0
|  | RS2579858 | Collector foil 5,8,10 | 1 | 5000 | 2573 |  | 2573 | 1500 | 0
|  | RS2579820 | Steam outlet hose | 1 | 5000 | 2573 |  | 2573 | 1500 | 0
|  | RS2579882 | Float assembly | 1 | 10000 | 2573 |  | 2573 | 1500 | 0
|  | RS2579888 | Hose set for level control 5-10 | 1 | 5000 | 2573 |  | 2573 | 1500 | 0
|  | RS2579893 | Steam hose nipple | 1 | 10000 | 2573 |  | 2573 | 1500 | 0
|  | 2579874 | Inlet Vv 5-10 | 1 | 20000 | 2573 |  | 2573 | 1500 | 0
|  | 2579856 | Cylinder insert with foil 5-10 | 1 | 10000 | 2573 |  | 2573 | 1500 | 0
|  | 2579884 | Water cup cpl. | 1 | 20000 | 2573 |  | 2573 | 1500 | 0
|  | 2579887 | Hose set for drain pump 5-10 | 1 | 20000 | 2573 |  | 2573 | 1500 | 0
|  | 2579885 | Hose set for inlet and drain 5-10 | 1 | 20000 | 2573 |  | 2573 | 1500 | 0
|  | 1115507 | Main Contactor 25A | 1 | 10000 | 2573 |  | 2573 | 1500 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1198363 | RS 5-10kg | DF1115497 | Snap ring large | 1 | 2500 | 110 |  | 110 | 500 | 0
|  | RS2599191 | Sealing set for tank | 1 | 2500 | 110 |  | 110 | 500 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 5000 | 110 |  | 110 | 500 | 0
|  | DF1101516 | Tank gasket 5-10 | 1 | 5000 | 110 |  | 110 | 500 | 0
|  | RS2579858 | Collector foil 5,8,10 | 1 | 5000 | 110 |  | 110 | 500 | 0
|  | RS2579820 | Steam outlet hose | 1 | 5000 | 110 |  | 110 | 500 | 0
|  | RS2579882 | Float assembly | 1 | 10000 | 110 |  | 110 | 500 | 0
|  | RS2579888 | Hose set for level control 5-10 | 1 | 5000 | 110 |  | 110 | 500 | 0
|  | RS2579893 | Steam hose nipple | 1 | 10000 | 110 |  | 110 | 500 | 0
|  | 2579874 | Inlet Vv 5-10 | 1 | 20000 | 110 |  | 110 | 500 | 0
|  | 2579856 | Cylinder insert with foil 5-10 | 1 | 10000 | 110 |  | 110 | 500 | 0
|  | 2579884 | Water cup cpl. | 1 | 20000 | 110 |  | 110 | 500 | 0
|  | 2579887 | Hose set for drain pump 5-10 | 1 | 20000 | 110 |  | 110 | 500 | 0
|  | 2579885 | Hose set for inlet and drain 5-10 | 1 | 20000 | 110 |  | 110 | 500 | 0
|  | 1115507 | Main Contactor 25A | 1 | 10000 | 110 |  | 110 | 500 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1198364 | RS 5-10kg | DF1115497 | Snap ring large | 1 | 2500 | 1153 |  | 1153 | 1000 | 0
|  | RS2599191 | Sealing set for tank | 1 | 2500 | 1153 |  | 1153 | 1000 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 5000 | 1153 |  | 1153 | 1000 | 0
|  | DF1101516 | Tank gasket 5-10 | 1 | 5000 | 1153 |  | 1153 | 1000 | 0
|  | RS2579858 | Collector foil 5,8,10 | 1 | 5000 | 1153 |  | 1153 | 1000 | 0
|  | RS2579820 | Steam outlet hose | 1 | 5000 | 1153 |  | 1153 | 1000 | 0
|  | RS2579882 | Float assembly | 1 | 10000 | 1153 |  | 1153 | 1000 | 0
|  | RS2579888 | Hose set for level control 5-10 | 1 | 5000 | 1153 |  | 1153 | 1000 | 0
|  | RS2579893 | Steam hose nipple | 1 | 10000 | 1153 |  | 1153 | 1000 | 0
|  | 2579874 | Inlet Vv 5-10 | 1 | 20000 | 1153 |  | 1153 | 1000 | 0
|  | 2579856 | Cylinder insert with foil 5-10 | 1 | 10000 | 1153 |  | 1153 | 1000 | 0
|  | 2579884 | Water cup cpl. | 1 | 20000 | 1153 |  | 1153 | 1000 | 0
|  | 2579887 | Hose set for drain pump 5-10 | 1 | 20000 | 1153 |  | 1153 | 1000 | 0
|  | 2579885 | Hose set for inlet and drain 5-10 | 1 | 20000 | 1153 |  | 1153 | 1000 | 0
|  | 1115507 | Main Contactor 25A | 1 | 10000 | 1153 |  | 1153 | 1000 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1200482 | RS 5-10kg | DF1115497 | Snap ring large | 1 | 2500 | 1418 |  | 1418 | 1100 | 1
|  | RS2599191 | Sealing set for tank | 1 | 2500 | 1418 |  | 1418 | 1100 | 1
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 5000 | 1418 |  | 1418 | 1100 | 0
|  | DF1101516 | Tank gasket 5-10 | 1 | 5000 | 1418 |  | 1418 | 1100 | 0
|  | RS2579858 | Collector foil 5,8,10 | 1 | 5000 | 1418 |  | 1418 | 1100 | 0
|  | RS2579820 | Steam outlet hose | 1 | 5000 | 1418 |  | 1418 | 1100 | 0
|  | RS2579882 | Float assembly | 1 | 10000 | 1418 |  | 1418 | 1100 | 0
|  | RS2579888 | Hose set for level control 5-10 | 1 | 5000 | 1418 |  | 1418 | 1100 | 0
|  | RS2579893 | Steam hose nipple | 1 | 10000 | 1418 |  | 1418 | 1100 | 0
|  | 2579874 | Inlet Vv 5-10 | 1 | 20000 | 1418 |  | 1418 | 1100 | 0
|  | 2579856 | Cylinder insert with foil 5-10 | 1 | 10000 | 1418 |  | 1418 | 1100 | 0
|  | 2579884 | Water cup cpl. | 1 | 20000 | 1418 |  | 1418 | 1100 | 0
|  | 2579887 | Hose set for drain pump 5-10 | 1 | 20000 | 1418 |  | 1418 | 1100 | 0
|  | 2579885 | Hose set for inlet and drain 5-10 | 1 | 20000 | 1418 |  | 1418 | 1100 | 0
|  | 1115507 | Main Contactor 25A | 1 | 10000 | 1418 |  | 1418 | 1100 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
1200481 | RS 5-10kg | DF1115497 | Snap ring large | 1 | 2500 | 77 |  | 77 | 250 | 0
|  | RS2599191 | Sealing set for tank | 1 | 2500 | 77 |  | 77 | 250 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 5000 | 77 |  | 77 | 250 | 0
|  | DF1101516 | Tank gasket 5-10 | 1 | 5000 | 77 |  | 77 | 250 | 0
|  | RS2579858 | Collector foil 5,8,10 | 1 | 5000 | 77 |  | 77 | 250 | 0
|  | RS2579820 | Steam outlet hose | 1 | 5000 | 77 |  | 77 | 250 | 0
|  | RS2579882 | Float assembly | 1 | 10000 | 77 |  | 77 | 250 | 0
|  | RS2579888 | Hose set for level control 5-10 | 1 | 5000 | 77 |  | 77 | 250 | 0
|  | RS2579893 | Steam hose nipple | 1 | 10000 | 77 |  | 77 | 250 | 0
|  | 2579874 | Inlet Vv 5-10 | 1 | 20000 | 77 |  | 77 | 250 | 0
|  | 2579856 | Cylinder insert with foil 5-10 | 1 | 10000 | 77 |  | 77 | 250 | 0
|  | 2579884 | Water cup cpl. | 1 | 20000 | 77 |  | 77 | 250 | 0
|  | 2579887 | Hose set for drain pump 5-10 | 1 | 20000 | 77 |  | 77 | 250 | 0
|  | 2579885 | Hose set for inlet and drain 5-10 | 1 | 20000 | 77 |  | 77 | 250 | 0
|  | 1115507 | Main Contactor 25A | 1 | 10000 | 77 |  | 77 | 250 | 0

## Spares Planning
Part Number | Part Name | No parts per unit | Site Spares | Required | SP
DF1115497 | Upper snap ring | 1 | 23 | 16 | -7
DF1115498 | Lower snap ring | 1 | 0 | 11 | 11
DF1101516 | Tank gasket 5-16 | 1 | 4 | 0 | -4
1119793 | Collector foil 5-16 | 1 | 0 | 0 | 0
DF1103817 | Steam outlet hose | 1 | 3 | 2 | -1
DF1115539 | Float assembly | 1 | 15 | 2 | -13
DF1115546 | Float hose | 1 | 0 | 11 | 11
DF2575607 | Drain coupling | 1 | 11 | 2 | -9
DF1115499 | Scale collector 5-16kg | 1 | 5 | 2 | -3
1115507 | Contactor | 1 | 0 | 2 | 2
DF1103675 | Steam hose (IDZ10 42mm) | 1 | 0 | 4 | 4
DF1103350 | Condensate hose | 1 | 0 | 4 | 4
1115489 | 5 - 16 Cylinder insert with grid | 1 | 5 | 3 | -2
1115535 | Inlet Vv | 1 | 0 | 5 | 5
1115503 | Steam Nipple | 1 | 0 | 5 | 5
1115476 | Element Single | 3 |  |  | 0
1115475 | Element 3pc | 1 |  |  | 0
DF2560304 | Element gaskets | 1 |  |  | 0
1115500 | Scale collector 20-40kg | 1 | 6 | 0 | -6
1115490 | 16-40 Cylinder insert with grid | 1 | 6 | 2 | -4
DF1119796 | Collector foil 20-80 | 1 | 0 | 6 | 6
DF1100966 | Tank gasket 20-80 | 1 | 1 | 0 | -1
1115509 | Contactor 30A | 1 | 1 | 3 | 2
1115511 | Contactor 50A | 1 | 0 | 1 | 1
RS2599191 | Sealing set for tank | 1 | 0 | 6 | 6
RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 0 | 2 | 2
RS2579858 | Collector foil 5,8,10 | 1 | 0 | 0 | 0
RS2579820 | Steam outlet hose | 1 | 0 | 2 | 2
RS2579882 | Float assembly | 1 | 0 | 0 | 0
RS2579888 | Hose set for level control 5-10 | 1 | 0 | 0 | 0
RS2579893 | Steam hose nipple | 1 | 0 | 0 | 0
2579874 | Inlet Vv 5-10 | 1 | 0 | 0 | 0
2579875 | Inlet Vv 16-40 | 1 | 0 | 0 | 0