## Parts
Please note that the information given below is only to act as a guide and the frequency of maintenance may depend upon the unit's age, usage and water quality. Correct maintenance is vital to ensure optimum output and reliability
Condair HPRO recommended preventive/critical spare parts guide
|  | HPRO200 VFD | Technical lifetime | 6 month | First year | 6 month | second year | 6 month | Third year | 6 month | Fourth year
Description | Part number
Water filter
Filter 5 micron 20" | PX05/20 | 1 | 6 months | Change | Change | Change | Change | Change | Change | Change | Change
O-ring for water filter | 430020050 | 1 | 24 months | Check | Check | Check | Change | Check | Check | Check | Change
Air Filter for RO tank
Sterile breather filter 0,2 my | 104581000 | 1 | 12 months | Check | Change | Check | Change | Check | Change | Check | Change
UV Filter (not on all Pump stations), 30 mJ/cm2
UV 10W | 104594000 | 1 | 12 months | Check | Change | Check | Change | Check | Change | Check | Change
Quarts UV System (not on all Pump stations)
Quartz Sleeves for UV 10W | 104582000 | 1 | 48 months | Check | Check | Check | Check | Check | Check | Check | Change
RO membrane
4" for MLPRO: water quality 250 µS and lower (most used) | MEM4040 | 1 | 95% efficiency | Check | Check | Check | Check | Check | Check | Check | TBR
Electrical control system
Print frame relay Pump and On/Off valve | 680010177 | 3 | 12 months |  | Change |  | Change |  | Change |  | Change
Contactor | 349010205 | 2 | 48 months |  | Check |  | Check |  | Check |  | Change
High pressure pump
Service kit for PAHT 2 | 104466001 | 1 | 8000h (24m critical) |  |  |  | OH - TBC |  |  |  | TBR
High pressure pump motor coupling
Service kit coupling PAHT 2/4 | 240020072 | 1 | 16000h (48m critical) |  |  |  | Check |  |  |  | Check
Valveblock (highpressure)
Repair kit for one valve; core, spring, o-rings | 190021030 | 4xVB | 36 months |  | Check |  | Check |  | Overhaul |  | Check
Repair kit for one valve; guide tube, core, spring, o-rings | 190021031 | 4xVB | 36 months |  | Check |  | Check |  | Check |  | Check
Pressure regulator
Service kit | 104481000 | 1 | 12 months | Check | Overhaul | Check | Overhaul | Check | Overhaul | Check | Overhaul
On/off valve
On/off valve rep kit 1/2" 10 bar_24V | 190020023 | 1 | 48 months | Check | Check | Check | Check | Check | Check | Check | Change
Check valve at manifold
Check valve 1/4" | 510020000 | 1 | 24 months | Check | Check | Check | Change | Check | Check | Check | Change
Nozzles
Nozzle ML 4.5 Stainless | 103150000 | 0,1 xN | 5-10 % yearly | Check | Check | Check | Check | Check | Check | Check | Check
Nozzle ML 2,5 Stainless | 103160000 | 0,1 xN | 5-10 % yearly | Check | Check | Check | Check | Check | Check | Check | Check
Water softener (not on all Pump stations)
Service kit Kinetico 30/2030 - 60/2060 | 150110002 | 1 | 24 months | Check | Check | Check | Change | Check | Check | Check | Change
Test set of softnes | 150400000 | 1 | 12 months | Check | Change | Check | Change | Check | Change | Check | Change
Ekstra water filter (not on all Pump stations)
Filter 20 micron 20" | PX20-20 | 1 | 6 months | Change | Change | Change | Change | Change | Change | Change | Change
Hygiene
Disinfection | MLHPDIS | 1 | 6 months | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Hygiene indication test (Condair only ) | ATPHYGIENE | 1 | 6 months | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes