## Mk5
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| Mk5 5kg | DF1115497 | Upper snap ring | 1 | 2500 |  |  | 0 |  | 0
|  | DF1115498 | Lower snap ring | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1115539 | Float assembly | 1 | 7500 | 0 |  | 0 | 0 | 0
|  | DF1115546 | Float hose | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | 1115507 | Contactor | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | DF1103350 | Condensate hose | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115535 | Inlet Vv | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 1115503 | Steam Nipple | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | 1115476 | Element Single | 3 | When less than 42ohms
|  | 1115475 | Element 3pc | 1 | When less than 42ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| Mk5 10kg | DF1115497 | Upper snap ring | 1 | 2500 |  |  | 0 | 0 | 0
|  | DF1115498 | Lower snap ring | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | DF1101516 | Tank gasket 5-16 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 1119793 | Collector foil 5-16 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1115539 | Float assembly | 1 | 7500 | 0 |  | 0 | 0 | 0
|  | DF1115546 | Float hose | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | DF1115499 | Scale collector 5-16kg | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | 1115507 | Contactor | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | DF1103350 | Condensate hose | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2557691 | 5 - 16 Cylinder insert with foil | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115535 | Inlet Vv | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 1115503 | Steam Nipple | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | 1115480 | Element Single | 3 | When less than 21ohms
|  | 1115479 | Element 3pc | 1 | When less than 21ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| Mk5 20kg | DF1115497 | Upper snap ring | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | DF1115498 | Lower snap ring | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | DF1100966 | Tank gasket 20-80 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1119796 | Collector foil 20-80 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1103817 | Steam outlet hose | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1115539 | Float assembly | 1 | 7500 | 0 |  | 0 | 0 | 0
|  | DF1115546 | Float hose | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | DF2575607 | Drain coupling | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | DF1115500 | Scale collector 20-40kg | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | 1115509 | 20kg Contactor | 2 | 15000 | 0 |  | 0 | 0 | 0
|  | DF1103675 | Steam hose (IDZ10 42mm) | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | DF1103350 | Condensate hose | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2557692 | 20kg Cylinder insert with foil | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1104535 | Inlet Vv | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 1115503 | Steam Nipple | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | 1115480 | Element Single | 3 | When less than 21ohms
|  | 1115479 | Element 3pc | 1 | When less than 21ohms
|  | DF2560304 | Element gaskets | 1 | When changing Elements

## EL
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| EL 5kg | 1115511 | Contactor | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 2584627 | Steam outlet | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 2584616 | Hose set | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 2579884 | Water cup cpl. | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 5020007 | A343 Low Cond Exchange cylinder | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 5020012 | A363 Norm Exchange cylinder | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 5020033 | D343 Low Cond Cleanable cylinder | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 5020036 | D363 Norm Cleanable cylinder | 1 | 5000 | 0 |  | 0 | 0 | 0
[6 empty] | 0 |  | 0 | 0 | 0
[6 empty] | 0 |  | 0 | 0 | 0
[6 empty] | 0 |  | 0 | 0 | 0
[6 empty] | 0 |  | 0 | 0 | 0
[6 empty] | 0 |  | 0 | 0 | 0
[6 empty] | 0 |  | 0 | 0 | 0
[6 empty] | 0 |  | 0 | 0 | 0

## HygroMatik
SN | Unit | Part Number | Part Name | No parts per unit | Frequency in Hours | Total Run | Last Changed | Hours run | Expected Hours | Required
| HY1 | E-3216010 | O-ring for cylinder flange | 1 | 2500
|  | E-3216011 | O-ring for cylinder base | 1 | 2500
|  | E-3220005 | O-ring for cylinder base pump adapter | 2 | 2500
|  | E-2404024 | O-ring for drain pump between housing and motor | 2 | 2500
|  | B-3204031 | Steam cylinder compl. | 1 | 5000
|  | E-2501005 | Main contactor 16 A, 230 V/ 50-60Hz | 1 | 10000
|  | E-2604014 | Connecting hose 0,9 | 1 | 10000
|  | E-3220000 | Cylinder base | 1 | 10000
|  | B-3216023 | Mounting set for cylinder base | 1 | 10000
|  | E-3221002 | Adapter for steam hose | 1 | 10000
|  | B-2304021 | Solenoid valve (Inlet) | 1 | 10000
|  | E-3320400 | Flow rate controller 2.5 l/min. (restrictor) | 1 | 10000
|  | E-2304029 | Fine filter for inlet | 1 | 10000
|  | B-3401017 | Drain hose set | 1 | 20000
|  | E-3221004 | Clip for adapter steam hose | 1 | 20000
|  | B-2404027 | Blow-down pump without mounting set | 1 | 20000
SN | Unit | Part Number | Part Name | No parts per unit | Frequency in Hours | Total Run | Last Changed | Hours run | Expected Hours | Required
| HY2 | E-2206050 | O-ring for cylinder flange | 1 | 2500
|  | E-2204022 | O-ring for cylinder base | 1 | 2500
|  | E-3220005 | O-ring for cylinder base pump adapter | 2 | 2500
|  | E-2404024 | O-ring for drain pump between housing and motor | 2 | 2500
|  | B-2204101 | Steam cylinder compl. | 1 | 5000
|  | E-2501005 | Main contactor 16 A, 230 V/ 50-60Hz | 1 | 10000
|  | E-2604014 | Connecting hose 1,6 | 1 | 10000
|  | E-2206086 | Cylinder base | 1 | 10000
|  | B-3216023 | Mounting set for cylinder base | 1 | 10000
|  | E-2209000 | Adapter for steam hose | 1 | 10000
|  | B-2304023 | Solenoid valve (Inlet) | 1 | 10000
|  | E-3320400 | Flow rate controller 2.5 l/min. (restrictor) | 1 | 10000
|  | E-2304029 | Fine filter for inlet | 1 | 10000
|  | B-3401019 | Drain hose set | 1 | 20000
|  | E-3221004 | Clip for adapter steam hose | 1 | 20000
|  | B-2404027 | Blow-down pump without mounting set | 1 | 20000

## Dri Steem
SN | Unit | Part Number | Part Name | No parts per unit | Frequency in Hours | Total Run | Last Changed | Hours run | Expected Hours | Required
HT

## CP3
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| CP3 | 1115809 | 52KG Unit Contactors | 2 | 10000 |  |  | 0 | 0 | 0
|  | 2530187 | Hose set inlet | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | 2530189 | Hose set pump | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 2530191 | Draining hose | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 5020025 | Exchange cylinder A674 | 2 | 5000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 5000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 10000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 10000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 15000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 15000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 20000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 20000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 10000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 20000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 | 15000 | 0 |  | 0 | 0 | 0
|  |  |  | 1 |  | 0 |  | 0 | 0 | 0
|  |  |  | 1 |  | 0 |  | 0 | 0 | 0
|  |  |  | 1 |  | 0 |  | 0 | 0 | 0
[7 empty] | 400 | 22500 | 56.25

## ELMC
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| ELMC | 42208L | Drain Valve Body | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 42207L | Drain Walve O-ring | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 42202LB | Drain Valve Solenoid | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 42427 | Water Inlet Valve | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 42419 | Inlet Valve Coil | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 42001 | Water Feed Hose 10mm | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 42003 | Water Feed Hose 15mm | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 42604 | Water Inlet Hose | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 42311 | High Water Level Boot | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 41902-1 | HWL Cable and Boot for 1 cylinder | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 41902-2 | HWL Cable and Boot for 2 cylinder | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 41903-3 | HWL Cable and Boot for 3 cylinder | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 41920 | Electrode Cable Set ELMC 5, 10, 20 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 41920A | Electrode Cable Set ELMC 30, 40 , 50, 60 + 90 | 1 | 20000 | 0
|  | 42114 | Cylinder Gasket 15-90 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 21300/MC | Contactor ELMC 5-10 | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 21301/MC | Contactor ELMC 20+40 | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 21302/MC | Contactor ELMC 30,50,60+90 | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | DIS/5 | Disposable Cylinder ELMC5 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DIS/8 | Disposable Cylinder ELMC8 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DIS/10 | Disposable Cylinder ELMC10 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DIS/20-96 | Disposable Cylinder ELMC20-90 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 42801 | Steam Hose 15mm ID Condensate | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 42802 | Steam Hose 25mm ID | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 42804 | Steam Hose 40mm ID | 1 | 20000 | 0 |  | 0 | 0 | 0

## ELMC2
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| ELMC2 | 930058 | Filling cup with hoses for ELMC 1 small sized cylinder | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | 930059 | Filling cup with hoses for ELMC 1 large sized cylinder | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | 930060 | Filling cup with hoses for ELMC 2 cylinders | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 930061 | Filling cup with hoses for ELMC 3 cylinders (left hand side) | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 930062 | Filling cup with hoses for ELMC 3 cylinders (right hand side) | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 930301 | Hose clamp Ø25x40mm | 1 | 7500 | 0 |  | 0 | 0 | 0
|  | 930302 | Hose clamp Ø40x60mm | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 930085 | Power cable kit n° 1 (3 single cables with sockets and boots) | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 930086 | Power cable kit n°2 (2 single cables + 1 split cable with sockets and boots) | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | 930087 | Power cable kit n° 3 (3 single cables + 1 split cable with sockets and boots) | 2 | 15000 | 0 |  | 0 | 0 | 0
|  | 930079 | Cylinder retaining clip ELMC small sized cylinder | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 930080 | Cylinder retaining clip ELMC large sized cylinder | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 930088 | High water level electrode cable ELMC 1 cylinder | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 930089 | High water level electrode cable ELMC 2 cylinders | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 930090 | High water level electrode cable ELMC 3 cylinders | 1 | 15000 | 0 |  | 0 | 0 | 0
|  | D61898 | Overflow hose Ø19/26mm (per meter)
|  | D61898 | Water feed hose Ø19/26mm (per meter)
|  | 930189 | Bag of 10 drain valve 0-rings
|  | 930153 | 230V complete drain valve
|  | 930307 | Plastic drain valve body
|  | 930220 | Drain valve stem with 230V solenoid
|  | 930161 | 230V solenoid
|  | 930072 | Drain cup upper half ELMC 1 cylinder, 2 cylinders left hand side, 3 cylinders right hand side
|  | 930074 | Drain cup upper half ELMC 2 cylinders right hand side, 90 middle
|  | 930075 | Drain cup upper half ELMC 3 cylinders left handside
|  | 930078 | Drain cup lower half
|  | 930084 | Water inlet hose
|  | 930150 | Inlet valve ELMC 1 small sized cylinder
|  | 930151 | Inlet valve ELMC 1 large sized cylinder
|  | 930152 | Inlet valve ELMC 3 cylinders
|  | 930160 | 230V inlet valve solenoid
|  | 930081 | Hose clamp Ø12x22mm
|  | 930082 | Hose clamp Ø16x27mm
|  | 930083 | Hose clamp Ø20x32mm
|  | D61899 | Water feed hose Ø13/18mm (per meter)
|  | 930190 | Brass nut Ø8mm
|  | 930148 | Bag of 3 fibre washers
|  | 930211 | High water level electrode + nut Ø4mm
|  | 930203 | Bag of bolts & nuts ELMC small sized cylinder (cleanable cylinder )
|  | 930223 | Bag of bolts & nuts ELMC large sized cylinder (cleanable cylinder)
|  | 930162 | Cylinder gasket ELMC small sized cylinder
|  | 930166 | Cylinder gasket ELMC large sized cylinder
|  | 930169 | Electrode plate divider ELMC large sized cylinder
|  | 930168 | Cylinder strainer ELMC small sized cylinder
|  | 930159 | Cylinder strainer ELMC large sized cylinder
|  | 930010 | Small sized disposable cylinder
|  | 930020 | Small sized isposable cylinder EA

## RS
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| RS 5-10kg | DF1115497 | Snap ring large | 1 | 2500 |  |  | 0 |  | 0
|  | RS2599191 | Sealing set for tank | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1101516 | Tank gasket 5-10 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579858 | Collector foil 5,8,10 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579820 | Steam outlet hose | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579888 | Hose set for level control 5-10 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579882 | Float assembly | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | RS2579893 | Steam hose nipple | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 2579856 | Cylinder insert with foil 5-10 | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115507 | Main Contactor 25A | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 2579874 | Inlet Vv 5-10 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579884 | Water cup cpl. | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579887 | Hose set for drain pump 5-10 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579885 | Hose set for inlet and drain 5-10 | 1 | 20000 | 0 |  | 0 | 0 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| RS 16-20kg | DF1115497 | Snap ring large | 1 | 2500 |  |  | 0 |  | 0
|  | RS2599191 | Sealing set for tank | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 1100966 | Tank gasket 16-40 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579820 | Steam outlet hose | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579882 | Float assembly | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | RS2579893 | Steam hose nipple | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115509 | Main Contactor 32A | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | DF1119796 | Collector foil 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579875 | Inlet Vv 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579884 | Water cup cpl. | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| RS 24-30kg | DF1115497 | Snap ring large | 1 | 2500 |  |  | 0 |  | 0
|  | RS2599191 | Sealing set for tank | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 1100966 | Tank gasket 16-40 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579820 | Steam outlet hose | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579882 | Float assembly | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | RS2579893 | Steam hose nipple | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115511 | Main Contactor 50A | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115509 | Secondary Contactor 32A | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | DF1119796 | Collector foil 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579875 | Inlet Vv 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579884 | Water cup cpl. | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| RS 40kg | DF1115497 | Snap ring large | 1 | 2500 |  |  | 0 |  | 0
|  | RS2599191 | Sealing set for tank | 1 | 2500 | 0 |  | 0 | 0 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | 1100966 | Tank gasket 16-40 | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579820 | Steam outlet hose | 1 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579882 | Float assembly | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | RS2579893 | Steam hose nipple | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1117502 | Main Contactor 80A | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115511 | Secondary Contactor 50A | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | DF1119796 | Collector foil 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579875 | Inlet Vv 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579884 | Water cup cpl. | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 1 | 20000 | 0 |  | 0 | 0 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| RS 50kg | DF1115497 | Snap ring large | 2 | 2500 |  |  | 0 |  | 0
|  | RS2599191 | Sealing set for tank | 2 | 2500 | 0 |  | 0 | 0 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | 1100966 | Tank gasket 16-40 | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1119796 | Collector foil 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | RS2579820 | Steam outlet hose | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579882 | Float assembly | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | RS2579893 | Steam hose nipple | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 2579875 | Inlet Vv 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 2579884 | Water cup cpl. | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 1115511 | Main Contactor 50A | 1 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115509 | Secondary Contactor 32A | 4 | 10000 | 0 |  | 0 | 0 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| RS 60kg | DF1115497 | Snap ring large | 2 | 2500 |  |  | 0 |  | 0
|  | RS2599191 | Sealing set for tank | 2 | 2500 | 0 |  | 0 | 0 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | 1100966 | Tank gasket 16-40 | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1119796 | Collector foil 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | RS2579820 | Steam outlet hose | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579882 | Float assembly | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | RS2579893 | Steam hose nipple | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 2579875 | Inlet Vv 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 2579884 | Water cup cpl. | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 1115511 | Main Contactor 50A | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115509 | Secondary Contactor 32A | 4 | 10000 | 0 |  | 0 | 0 | 0
SN | Unit | Part Number | Part Name | No parts per unit | Frequency | Total Run | Last Changed | Hours run | Expected Hours | Required
| RS 80kg | DF1115497 | Snap ring large | 2 | 2500 |  |  | 0 |  | 0
|  | RS2599191 | Sealing set for tank | 2 | 2500 | 0 |  | 0 | 0 | 0
|  | RS2599233 | Scale collector & connection ring, Includes sealing set. | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | 1100966 | Tank gasket 16-40 | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | DF1119796 | Collector foil 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | RS2579820 | Steam outlet hose | 2 | 5000 | 0 |  | 0 | 0 | 0
|  | RS2579882 | Float assembly | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | RS2579899 | Hose set for level control 16 - 40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | RS2579893 | Steam hose nipple | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 2579875 | Inlet Vv 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 2557692 | Cylinder insert with foil 16-40 | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 2579884 | Water cup cpl. | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579898 | Hose set for drain pump 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 2579896 | Hose set for inlet and drain 16-40 | 2 | 20000 | 0 |  | 0 | 0 | 0
|  | 1117502 | Main Contactor 80A | 2 | 10000 | 0 |  | 0 | 0 | 0
|  | 1115511 | Secondary Contactor 50A | 4 | 10000 | 0 |  | 0 | 0 | 0